## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.7035 | Magnet | 5.984 | 5984.001 | 5948.3111 | 10 | 0.885 | 21.9 |  | 0.885 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 22.3646 | Aperture1 | 2.9924 | 2992.379 | 2974.5318 | 100 | 3.05 | 20.5 |  | 3.08 | 20.5
[9 empty] | YT121 | 20.1919 | Aperture2 | 2.9916 | 2991.592 | 2973.7495 | 1000 | 0.632 | 6.05 |  | 0.735 | 6.74
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.5417 | Apt1 Pup | 1.4975 | 1497.462 | 1488.5308
CERN PART NUMBER : |  |  | HCMBBR_A00101 |  | Serial Number : |  | 000043 |  | YT211 | 20.9132 | Apt1 Plw | 1.4949 | 1494.899 | 1485.9831 | 10 | 0.885 | 21.8 |  | 0.886 | 21.9
[9 empty] | YT212 | 20.7335 | Apt2 Pup | 1.4967 | 1496.684 | 1487.7575 | 100 | 3.05 | 20.5 |  | 3.09 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.9721 | Apt2 Plw | 1.4949 | 1494.879 | 1485.9632 | 1000 | 0.621 | 5.92 |  | 0.776 | 6.82
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.2929
[15 empty] | 10 | 0.887 | 43.7 |  | 0.888 | 43.8
NAME OF TEST OPERATOR: |  |  | JARDOT | [11 empty] | 100 | 3.07 | 41.1 |  | 3.09 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.623 | 11.9 |  | 0.751 | 13.5
DATE OF TEST : |  |  | 29/09/2003 |  | TIME :
[15 empty] | 10 | 0.889 | 87.5
[15 empty] | 100 | 3.08 | 82.2
[15 empty] | 1000 | 0.683 | 25.4
TEST REALISE AVEC NOUVELLE ALIM KEPKO ET FREQUENCEMETRE SOLARTRON
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 21.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 33 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1497.462 | 1494.899 |  | 1496.684 | 1494.879
Poles [20°C] |  |  | 1488.5308 | 1485.9831 |  | 1487.7575 | 1485.9632
D1 & D2 |  |  | 2974.5318 | mW |  | 2973.7495 | mW
Magnet |  |  |  | 5948.3111 | mW
|  | Poles Nr. | JP 165 | JP 166 |  | JP 167 | JP 168
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.7035 | 20.1919 |  | 20.9132 | 20.9721
|  |  | 22.3646 | 21.5417 |  | 20.7335 | 21.2929
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 270 | nF |  | 250 | nF
D1 & D2 -----> Ground |  |  | 210 | nF |  | 210 | nF
Magnet -----> Ground |  |  |  | 360 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000043 |  |  |  |  | Date: | 29/09/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.885 | 0.885 |  | 0.885 | 0.886
D1 & D2 |  | (L) | 43.7 | mH |  | 43.8 | mH
|  | (Q) | 0.887 |  |  | 0.888
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.889
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.5 |  | 20.5 | 20.5
|  | (Q) | 3.05 | 3.05 |  | 3.07 | 3.09
D1 & D2 |  | (L) | 41.1 | mH |  | 41.1 | mH
|  | (Q) | 3.07 |  |  | 3.09
Magnet |  |  | (L) | 82.2 | mH
|  |  | (Q) | 3.08
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.05 | 5.92 |  | 6.74 | 6.82
|  | (Q) | 0.632 | 0.621 |  | 0.735 | 0.776
D1 & D2 |  | (L) | 11.9 | mH |  | 13.5 | mH
|  | (Q) | 0.623 |  |  | 0.751
Magnet |  |  | (L) | 25.4 | mH
|  |  | (Q) | 0.683
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000043 |  |  |  |  | Date: | 29/09/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 9.3 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 10.8 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 2.02 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 2.2 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 3.38 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 3.68 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.4 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.2 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.956 | 0.952 |  | 0.948 | 0.958
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.64 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 395 | 349 | µS | 349 | 348 | µS
| [C= 2µF] | Current | 37 | 38.5 | A | 38 | 40 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION