## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.0924 | Magnet | 6.0205 | 6020.458 | 5890.8591 | 10 | 0.89 | 21.9 |  | 0.892 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 20.581 | Aperture1 | 3.0135 | 3013.475 | 2948.6057 | 100 | 3.11 | 20.6 |  | 3.13 | 20.6
[9 empty] | YT121 | 21.1352 | Aperture2 | 3.007 | 3006.995 | 3006.995 | 1000 | 0.763 | 7.12 |  | 0.801 | 7.26
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 20.659 | Apt1 Pup | 1.5093 | 1509.308 | 1476.818
CERN PART NUMBER : |  |  | HCMBB_A00101 |  | Serial Number : |  | 000049 |  | YT211 | 20.7709 | Apt1 Plw | 1.5042 | 1504.156 | 1471.7769 | 10 | 0.892 | 21.8 |  | 0.893 | 21.9
[9 empty] | YT212 | 20.8317 | Apt2 Pup | 1.5045 | 1504.536 | 1472.1487 | 100 | 3.11 | 20.5 |  | 3.13 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.6509 | Apt2 Plw | 1.5024 | 1502.444 | 1470.1018 | 1000 | 0.766 | 7.06 |  | 0.828 | 7.24
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.6063
[15 empty] | 10 | 0.894 | 43.7 |  | 0.896 | 43.8
NAME OF TEST OPERATOR: |  |  | HENRY/JARDOT | [11 empty] | 100 | 3.12 | 41.1 |  | 3.14 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.757 | 14.1 |  | 0.811 | 14.5
DATE OF TEST : |  |  | 2003-12-06 |  | TIME :
[15 empty] | 10 | 0.896 | 87.6
[15 empty] | 100 | 3.13 | 82.3
[15 empty] | 1000 | 0.782 | 28.6
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 25.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 54 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1542.45 | 1542.1 |  | 1541.16 | 1540.63
Poles [20°C] |  |  | 1509.24 | 1508.9 |  | 1507.98 | 1507.46
D1 & D2 |  |  | 3084.57 | mW |  | 3082.01 | mW
Magnet |  |  |  | 6166.58 | mW
|  | Poles Nr. | JP 193 | JP 194 |  | JP 195 | JP 196
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 24.6 | 24.24 |  | 24.5 | 24.63
|  |  | 24.59 | 24.56 |  | 24.78 | 24.59
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000049 |  |  |  |  | Date: | 2003-12-06
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.852 | 0.851 |  | 0.852 | 0.851
D1 & D2 |  | (L) | 43.7 | mH |  | 43.8 | mH
|  | (Q) | 0.853 |  |  | 0.854
Magnet |  |  | (L) | 87.6 | mH
|  |  | (Q) | 0.856
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 19 | 19 |  | 19 | 19
|  | (Q) | 2.16 | 2.2 |  | 2.21 | 2.21
D1 & D2 |  | (L) | 38.1 | mH |  | 38.1 | mH
|  | (Q) | 2.2 |  |  | 2.21
Magnet |  |  | (L) | 76.3 | mH
|  |  | (Q) | 2.2
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 4.32 | 4.4 |  | 4.51 | 4.53
|  | (Q) | 0.666 | 0.671 |  | 0.692 | 0.713
D1 & D2 |  | (L) | 8.77 | mH |  | 9 | mH
|  | (Q) | 0.665 |  |  | 0.698
Magnet |  |  | (L) | 17.7 | mH
|  |  | (Q) | 0.679
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000049 |  |  |  |  | Date: | 2003-12-06
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 30.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 16.5 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 16.2 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 10.8 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 28.2 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 23 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.5 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.7 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.6 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.7 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.8 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.856 | 0.868 |  | 0.856 | 0.858
| Dipoles D1 & D2 [4KV] |  | 1.78 | mS |  | 1.77 | mS
| Magnet [4KV] |  |  | 2.68 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 487 | 487 | µS | 493 | 498 | µS
| [C= 2µF] | Current | 31 | 33 | A | 34.5 | 34.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION