## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.2396 | Magnet | 6.0166 | 6016.63 | 5945.2866 | 10 | 0.874 | 21.9 |  | 0.874 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 21.1377 | Aperture1 | 3.0082 | 3008.188 | 2972.5178 | 100 | 2.2 | 19 |  | 2.2 | 19
[9 empty] | YT121 | 22.0417 | Aperture2 | 3.0084 | 3008.437 | 3008.437 | 1000 | 0.665 | 4.35 |  | 0.693 | 4.45
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 22.0026 | Apt1 Pup | 1.5047 | 1504.655 | 1486.8132
CERN PART NUMBER : |  |  | HCMBARA00101 |  | Serial Number : |  | 000055 |  | YT211 | 22.2106 | Apt1 Plw | 1.5035 | 1503.519 | 1485.6907 | 10 | 0.873 | 21.8 |  | 0.873 | 21.9
[9 empty] | YT212 | 22.0974 | Apt2 Pup | 1.5054 | 1505.408 | 1487.5573 | 100 | 2.2 | 18.9 |  | 2.2 | 18.9
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 22.07 | Apt2 Plw | 1.503 | 1503.016 | 1485.1937 | 1000 | 0.671 | 4.36 |  | 0.709 | 4.47
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.0592
[15 empty] | 10 | 0.877 | 43.7 |  | 0.877 | 43.7
NAME OF TEST OPERATOR: |  |  | JARDOT | [11 empty] | 100 | 2.2 | 37.9 |  | 2.21 | 38
NAME OF RESPONSIBLE: | [8 empty] | Min | 21.1377 |  |  |  |  | 1000 | 0.665 | 8.69 |  | 0.699 | 8.92
DATE OF TEST : |  |  | 22/07/2003 |  | TIME : |  |  |  | Max | 22.2106
[9 empty] | Avg. | 21.6741 |  |  |  |  | 10 | 0.877 | 87.5
[15 empty] | 100 | 2.2 | 76
[15 empty] | 1000 | 0.68 | 17.6
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 23 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 68 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1504.655 | 1503.519 |  | 1505.408 | 1503.016
Poles [20°C] |  |  | 1486.8132 | 1485.6907 |  | 1487.5573 | 1485.1937
D1 & D2 |  |  | 2972.5178 | mW |  | 3008.437 | mW
Magnet |  |  |  | 5945.2866 | mW
|  | Poles Nr. | JP218 | JP221 |  | JP219 | JP220
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.2396 | 22.0417 |  | 22.2106 | 22.07
|  |  | 21.1377 | 22.0026 |  | 22.0974 | 22.0592
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 210 | nF
Magnet -----> Ground |  |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000055 |  |  |  |  | Date: | 22/07/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.874 | 0.873 |  | 0.874 | 0.873
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.877 |  |  | 0.877
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.877
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 19 | 18.9 |  | 19 | 18.9
|  | (Q) | 2.2 | 2.2 |  | 2.2 | 2.2
D1 & D2 |  | (L) | 37.9 | mH |  | 38 | mH
|  | (Q) | 2.2 |  |  | 2.21
Magnet |  |  | (L) | 76 | mH
|  |  | (Q) | 2.2
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 4.35 | 4.36 |  | 4.45 | 4.47
|  | (Q) | 0.665 | 0.671 |  | 0.693 | 0.709
D1 & D2 |  | (L) | 8.69 | mH |  | 8.92 | mH
|  | (Q) | 0.665 |  |  | 0.699
Magnet |  |  | (L) | 17.6 | mH
|  |  | (Q) | 0.68
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000055 |  |  |  |  | Date: | 22/07/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 23 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 17.7 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 10.3 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 7.55 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 22 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 12 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.1 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.962 | 0.952 |  | 0.958 | 0.956
| Dipoles D1 & D2 [4KV] |  | 1.76 | mS |  | 1.76 | mS
| Magnet [4KV] |  |  | 2.64 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 381 | 361 | µS | 360 | 362 | µS
| [C= 2µF] | Current | 36 | 39 | A | 38.5 | 38 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION