## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 24.0229 | Magnet | 6.0512 | 6051.164 | 5979.4111 | 10 | 0.876 | 21.9 |  | 0.877 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 24.0583 | Aperture1 | 3.026 | 3025.969 | 2990.0879 | 100 | 3.15 | 20.6 |  | 3.16 | 20.7
[9 empty] | YT121 | 24.063 | Aperture2 | 3.0252 | 3025.209 | 2989.337 | 1000 | 0.775 | 7.32 |  | 0.817 | 7.49
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 24.1575 | Apt1 Pup | 1.514 | 1513.985 | 1496.0326
CERN PART NUMBER : |  |  | HCMBA_A00101 |  | Serial Number : |  | 000060 |  | YT211 | 24.1158 | Apt1 Plw | 1.512 | 1511.986 | 1494.0573 | 10 | 0.877 | 21.9 |  | 0.876 | 21.9
[9 empty] | YT212 | 24.9692 | Apt2 Pup | 1.5129 | 1512.896 | 1494.9565 | 100 | 3.13 | 20.6 |  | 3.16 | 20.6
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 24.71 | Apt2 Plw | 1.5123 | 1512.317 | 1494.3844 | 1000 | 0.778 | 7.28 |  | 0.84 | 7.45
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 24.8907
[15 empty] | 10 | 0.879 | 43.7 |  | 0.88 | 43.8
NAME OF TEST OPERATOR: |  |  | HENRY/GUTOWSKI/JARDOT | [11 empty] | 100 | 3.16 | 41.3 |  | 3.16 | 41.3
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.775 | 14.6 |  | 0.825 | 14.9
DATE OF TEST : |  |  | 2003-10-09 |  | TIME :
[15 empty] | 10 | 0.881 | 87.6
[15 empty] | 100 | 3.16 | 82.5
[15 empty] | 1000 | 0.793 | 29.4
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 23 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 50 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1513.985 | 1511.986 |  | 1512.896 | 1512.317
Poles [20°C] |  |  | 1496.0326 | 1494.0573 |  | 1494.9565 | 1494.3844
D1 & D2 |  |  | 2990.0879 | mW |  | 2989.337 | mW
Magnet |  |  |  | 5979.4111 | mW
|  | Poles Nr. | JP 238 | JP 239 |  | JP 240 | JP 241
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 24.0229 | 24.063 |  | 24.1158 | 24.71
|  |  | 24.0583 | 24.1575 |  | 24.9692 | 24.8907
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 190 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000060 |  |  |  |  | Date: | 2003-10-09
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.9 |  | 21.9 | 21.9
|  | (Q) | 0.876 | 0.877 |  | 0.877 | 0.876
D1 & D2 |  | (L) | 43.7 | mH |  | 43.8 | mH
|  | (Q) | 0.879 |  |  | 0.88
Magnet |  |  | (L) | 87.6 | mH
|  |  | (Q) | 0.881
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.6 |  | 20.7 | 20.6
|  | (Q) | 3.15 | 3.13 |  | 3.16 | 3.16
D1 & D2 |  | (L) | 41.3 | mH |  | 41.3 | mH
|  | (Q) | 3.16 |  |  | 3.16
Magnet |  |  | (L) | 82.5 | mH
|  |  | (Q) | 3.16
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 7.32 | 7.28 |  | 7.49 | 7.45
|  | (Q) | 0.775 | 0.778 |  | 0.817 | 0.84
D1 & D2 |  | (L) | 14.6 | mH |  | 14.9 | mH
|  | (Q) | 0.775 |  |  | 0.825
Magnet |  |  | (L) | 29.4 | mH
|  |  | (Q) | 0.793
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000060 |  |  |  |  | Date: | 2003-10-09
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 27.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 26.2 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 14.1 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 12.3 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 24.6 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 22 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.9 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.4 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.974 | 0.964 |  | 0.966 | 0.952
| Dipoles D1 & D2 [4KV] |  | 1.8 | mS |  | 1.79 | mS
| Magnet [4KV] |  |  | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 518 | 522 | µS | 533 | 543 | µS
| [C= 2µF] | Current | 38.5 | 38.5 | A | 39.5 | 39 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION