## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 20.4478 | Magnet | 6.1482 | 6148.192 | 6051.3701 | 10 | 0.871 | 21.9 |  | 0.872 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 20.4541 | Aperture1 | 3.074 | 3073.96 | 3025.5512 | 100 | 3.1 | 20.6 |  | 3.14 | 20.6
[9 empty] | YT121 | 20.9843 | Aperture2 | 3.0743 | 3074.275 | 3025.8612 | 1000 | 0.761 | 7.16 |  | 0.81 | 7.38
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.0219 | Apt1 Pup | 1.5398 | 1539.771 | 1515.5226
CERN PART NUMBER : |  |  | HCMBAR_A00101 |  | Serial Number : |  | 000064 |  | YT211 | 21.1931 | Apt1 Plw | 1.5342 | 1534.191 | 1510.0305 | 10 | 0.873 | 21.8 |  | 0.871 | 21.9
[9 empty] | YT212 | 22.8016 | Apt2 Pup | 1.5392 | 1539.219 | 1514.9793 | 100 | 3.11 | 20.6 |  | 3.12 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 21.0082 | Apt2 Plw | 1.535 | 1535.044 | 1510.8701 | 1000 | 0.769 | 7.12 |  | 0.835 | 7.35
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.0128
[15 empty] | 10 | 0.875 | 43.7 |  | 0.875 | 43.8
NAME OF TEST OPERATOR: |  |  | JARDOT/GUTOWSKI | [11 empty] | 100 | 3.12 | 41.2 |  | 3.15 | 41.2
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.758 | 14.2 |  | 0.814 | 14.7
DATE OF TEST : |  |  | 24/9/2003 |  | TIME :
[15 empty] | 10 | 0.876 | 87.6
[15 empty] | 100 | 3.13 | 82.4
[15 empty] | 1000 | 0.785 | 28.9
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 24 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 41 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1539.771 | 1534.191 |  | 1539.219 | 1535.044
Poles [20°C] |  |  | 1515.5226 | 1510.0305 |  | 1514.9793 | 1510.8701
D1 & D2 |  |  | 3025.5512 | mW |  | 3025.8612 | mW
Magnet |  |  |  | 6051.3701 | mW
|  | Poles Nr. | JP 255 | JP 257 |  | JP 254 | JP 256
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 20.4478 | 20.9843 |  | 21.1931 | 21.0082
|  |  | 20.4541 | 21.0219 |  | 22.8016 | 21.0128
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 210 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 340 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000064 |  |  |  |  | Date: | 24/9/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.871 | 0.873 |  | 0.872 | 0.871
D1 & D2 |  | (L) | 43.7 | mH |  | 43.8 | mH
|  | (Q) | 0.875 |  |  | 0.875
Magnet |  |  | (L) | 87.6 | mH
|  |  | (Q) | 0.876
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.6 |  | 20.6 | 20.5
|  | (Q) | 3.1 | 3.11 |  | 3.12 | 3.12
D1 & D2 |  | (L) | 41.2 | mH |  | 41.2 | mH
|  | (Q) | 3.12 |  |  | 3.15
Magnet |  |  | (L) | 82.4 | mH
|  |  | (Q) | 3.13
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 7.16 | 7.12 |  | 7.38 | 7.35
|  | (Q) | 0.761 | 0.769 |  | 0.81 | 0.835
D1 & D2 |  | (L) | 14.2 | mH |  | 14.7 | mH
|  | (Q) | 0.758 |  |  | 0.814
Magnet |  |  | (L) | 28.9 | mH
|  |  | (Q) | 0.785
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000064 |  |  |  |  | Date: | 24/9/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 10.4 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 10.4 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 2.26 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 2.02 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 7.1 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 6.4 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.3 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.6 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.984 | 0.974 |  | 0.974 | 0.976
| Dipoles D1 & D2 [4KV] |  | 1.8 | mS |  | 1.81 | mS
| Magnet [4KV] |  |  | 2.71 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 408 | 426 | µS | 447 | 439 | µS
| [C= 2µF] | Current | 40.5 | 39 | A | 40.5 | 39.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION