## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 21.5953 | Magnet | 6.0697 | 6069.723 | 6081.8868 | 10 | 0.887 | 21.8 |  | 0.888 | 21.9
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 21.7661 | Aperture1 | 3.0358 | 3035.821 | 3041.9048 | 100 | 3.15 | 20.6 |  | 3.14 | 20.6
[9 empty] | YT121 | 20.2781 | Aperture2 | 3.0339 | 3033.86 | 3039.9399 | 1000 | 0.774 | 7.29 |  | 0.814 | 7.43
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.5699 | Apt1 Pup | 1.5184 | 1518.36 | 1521.4028
CERN PART NUMBER : |  |  | HCMBA_A00101 |  | Serial Number : |  | 000067 |  | YT211 | 21.0153 | Apt1 Plw | 1.5174 | 1517.422 | 1520.4629 | 10 | 0.886 | 21.8 |  | 0.886 | 21.9
[9 empty] | YT212 | 20.54 | Apt2 Pup | 1.517 | 1517.039 | 1520.0792 | 100 | 3.13 | 20.5 |  | 3.16 | 20.5
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.2937 | Apt2 Plw | 1.5168 | 1516.784 | 1519.8236 | 1000 | 0.775 | 7.21 |  | 0.839 | 7.41
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.7306
[15 empty] | 10 | 0.889 | 43.7 |  | 0.89 | 43.7
NAME OF TEST OPERATOR: |  |  | JARDOT/GUTOWSKI | [11 empty] | 100 | 3.15 | 41.1 |  | 3.16 | 41.1
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.766 | 14.4 |  | 0.82 | 14.8
DATE OF TEST : |  |  | 23/10/2003 |  | TIME :
[15 empty] | 10 | 0.891 | 87.5
[15 empty] | 100 | 3.16 | 82.3
[15 empty] | 1000 | 0.792 | 29.2
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 19.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 32 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1518.36 | 1517.422 |  | 1517.039 | 1516.784
Poles [20°C] |  |  | 1521.4028 | 1520.4629 |  | 1520.0792 | 1519.8236
D1 & D2 |  |  | 3041.9048 | mW |  | 3039.9399 | mW
Magnet |  |  |  | 6081.8868 | mW
|  | Poles Nr. | JP 266 | JP 267 |  | JP 268 | JP 269
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 21.5953 | 20.2781 |  | 21.0153 | 20.2937
|  |  | 21.7661 | 21.5699 |  | 20.54 | 21.7306
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 210 | nF |  | 210 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000067 |  |  |  |  | Date: | 23/10/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.9 | 21.9
|  | (Q) | 0.887 | 0.886 |  | 0.888 | 0.886
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.889 |  |  | 0.89
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.891
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.6 | 20.5 |  | 20.6 | 20.5
|  | (Q) | 3.15 | 3.13 |  | 3.15 | 3.16
D1 & D2 |  | (L) | 41.1 | mH |  | 41.1 | mH
|  | (Q) | 3.15 |  |  | 3.16
Magnet |  |  | (L) | 82.3 | mH
|  |  | (Q) | 3.16
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 7.29 | 7.21 |  | 7.43 | 7.41
|  | (Q) | 0.774 | 0.775 |  | 0.814 | 0.839
D1 & D2 |  | (L) | 14.4 | mH |  | 14.8 | mH
|  | (Q) | 0.766 |  |  | 0.82
Magnet |  |  | (L) | 29.2 | mH
|  |  | (Q) | 0.792
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000067 |  |  |  |  | Date: | 23/10/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 11.8 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 11.4 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 2.56 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 2.58 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 8.4 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 8.35 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.3 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.964 | 0.97 |  | 0.968 | 0.974
| Dipoles D1 & D2 [4KV] |  | 1.79 | mS |  | 1.79 | mS
| Magnet [4KV] |  |  | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 469 | 449 | µS | 437 | 432 | µS
| [C= 2µF] | Current | 39 | 39.5 | A | 42 | 39.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION