## Coils-Coll.
ELECTRICAL TESTS OF DIPOLES | [11 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
(WITH BEAM TUBES) | [9 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ALSTOM |  | CONTRACT NUMBER : F461 |  |  |  | YT111 | 20.1795 | Magnet | 5.9547 | 5954.713 | 5990.6569 | 10 | 0.891 | 21.8 |  | 0.891 | 21.8
SUB CONTRACTOR : |  |  | Jeumont Industrie |  | CONTRACT NUMBER : F461 |  |  |  | YT112 | 20.2197 | Aperture1 | 2.9777 | 2977.656 | 2995.6298 | 100 | 3.08 | 20.5 |  | 3.08 | 20.5
[9 empty] | YT121 | 20.1838 | Aperture2 | 2.9771 | 2977.062 | 2995.0322 | 1000 | 0.759 | 6.94 |  | 0.797 | 7.07
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.4015 | Apt1 Pup | 1.4895 | 1489.47 | 1498.4608
CERN PART NUMBER : |  |  | HCMBA_A00101 |  | Serial Number : |  | 000079 |  | YT211 | 20.2275 | Apt1 Plw | 1.4882 | 1488.186 | 1497.169 | 10 | 0.89 | 21.8 |  | 0.89 | 21.9
[9 empty] | YT212 | 20.0578 | Apt2 Pup | 1.4886 | 1488.552 | 1497.5372 | 100 | 3.06 | 20.4 |  | 3.07 | 20.4
CERN INSPECTION & TEST PLAN NUMBER : ITP Step 9a to 9l |  |  |  |  | TEST NUMBER : |  | 9a to 9l |  | YT221 | 20.2011 | Apt2 Plw | 1.4885 | 1488.5 | 1497.4849 | 1000 | 0.76 | 6.88 |  | 0.823 | 7.06
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.3019
[15 empty] | 10 | 0.894 | 43.7 |  | 0.894 | 43.7
NAME OF TEST OPERATOR: |  |  | JARDOT/GUTOWSKI | [11 empty] | 100 | 3.08 | 41 |  | 3.09 | 40.9
NAME OF RESPONSIBLE: | [14 empty] | 1000 | 0.753 | 13.8 |  | 0.805 | 14.1
DATE OF TEST : |  |  | 18/11/2003 |  | TIME :
[15 empty] | 10 | 0.895 | 87.4
[15 empty] | 100 | 3.09 | 81.9
[15 empty] | 1000 | 0.777 | 27.8
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 39 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1489.47 | 1488.186 |  | 1488.552 | 1488.5
Poles [20°C] |  |  | 1498.4608 | 1497.169 |  | 1497.5372 | 1497.4849
D1 & D2 |  |  | 2995.6298 | mW |  | 2995.0322 | mW
Magnet |  |  |  | 5990.6569 | mW
|  | Poles Nr. | JP 314 | JP 315 |  | JP 316 | JP 317
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  |  | 20.1795 | 20.1838 |  | 20.2275 | 20.2011
|  |  | 20.2197 | 21.4015 |  | 20.0578 | 20.3019
Capacitance |  |  | ITP step 9d & 9e
[ Megger 1000V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs -----> Dipoles |  |  | 200 | nF |  | 200 | nF
D1 & D2 -----> Ground |  |  | 200 | nF |  | 200 | nF
Magnet -----> Ground |  |  |  | 320 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000079 |  |  |  |  | Date: | 18/11/2003
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.9
|  | (Q) | 0.891 | 0.89 |  | 0.891 | 0.89
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.894 |  |  | 0.894
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.895
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 20.5 | 20.4 |  | 20.5 | 20.4
|  | (Q) | 3.08 | 3.06 |  | 3.08 | 3.07
D1 & D2 |  | (L) | 41 | mH |  | 40.9 | mH
|  | (Q) | 3.08 |  |  | 3.09
Magnet |  |  | (L) | 81.9 | mH
|  |  | (Q) | 3.09
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 6.94 | 6.88 |  | 7.07 | 7.06
|  | (Q) | 0.759 | 0.76 |  | 0.797 | 0.823
D1 & D2 |  | (L) | 13.8 | mH |  | 14.1 | mH
|  | (Q) | 0.753 |  |  | 0.805
Magnet |  |  | (L) | 27.8 | mH
|  |  | (Q) | 0.777
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
Serial Nr: | 000079 |  |  |  |  | Date: | 18/11/2003
INSULATION RESISTANCE
Dipole D1 + QHs D1 -----> Masse |  |  |  | 13.3 | GW |  | >1000MW
[V=1.0.KV, 1']
Dipole D2 + QHs D2 -----> Masse |  |  |  | 13.3 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D1(8x) -----> D1 |  |  | 4.72 | GW |  | >1000MW
[V=1.0.KV, 1']
| QHs D2(8x) -----> D2 |  |  | 3.18 | GW |  | >1000MW
[V=1.0.KV, 1']
DIPOLE 1
| POLE UP ------> POLE LW |  |  | 13.1 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 12.2 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS |  |  | ITP step 9f to 9h
Dipole D1 + QHs D1 -----> Masse |  |  |  | 0.1 | µA |  | <15.0µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 -----> Masse |  |  |  | 0.2 | µA |  | <15.0µA
[V=6.0KV 5' ]
| QHs D1(8x) -----> D1 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
| QHs D2(8x) -----> D2 |  |  | 0.1 | µA |  | <10.0µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  |  | 0.4 | µA |  | <10.0µA
[V=3.KV 5']
DIPOLE 2
| POLE UP ------> POLE LW |  |  | 0.5 | µA |  | <10.0µA
[V= 3KV 5']
DISCHARGE TEST |  |  | ITP step 9i & 9l
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] |  | 0.964 | 0.966 |  | 0.964 | 0.97
| Dipoles D1 & D2 [4KV] |  | 1.8 | mS |  | 1.8 | mS
| Magnet [4KV] |  |  | 2.7 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1600KV] |  | 416 | 450 | µS | 420 | 429 | µS
| [C= 2µF] | Current | 38.5 | 38 | A | 38 | 40 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION