## 2062
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F462 |  |  |  | YT111 | 22.3505 | Magnet | 6.0666 | 6066.563 | 6127.8414 | 10 | 0.907 | 22 |  | 0.908 | 22
SUB CONTRACTOR : | [8 empty] | YT112 | 22.3713 | Aperture1 | 3.0308 | 3030.793 | 3061.4071 | 100 | 4.52 | 21.5 |  | 4.59 | 21.5
[9 empty] | YT121 | 21.8173 | Aperture2 | 3.0358 | 3035.768 | 3066.4323 | 1000 | 1.61 | 14.6 |  | 1.63 | 14.6
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.814 | Apt1 Pup | 1.5144 | 1514.36 | 1529.6566
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 2062 |  | YT211 | 21.0901 | Apt1 Plw | 1.5164 | 1516.43 | 1531.7475 | 10 | 0.901 | 22.1 |  | 0.901 | 22
[9 empty] | YT212 | 21.0578 | Apt2 Pup | 1.5166 | 1516.625 | 1531.9444 | 100 | 4.61 | 21.5 |  | 4.54 | 21.5
CERN INSPECTION & TEST PLAN NUMBER : 9a To 9i |  |  |  |  | TEST NUMBER : |  | 9a to 9i |  | YT221 | 21.7035 | Apt2 Plw | 1.5191 | 1519.137 | 1534.4818 | 1000 | 1.64 | 14.4 |  | 1.64 | 14.4
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.8454
[15 empty] | 10 | 0.9 | 44 |  | 0.906 | 44.1
NAME OF TEST OPERATOR: |  |  | M.Levrero | [11 empty] | 100 | 4.57 | 42.9 |  | 4.55 | 42.9
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 1.63 | 29 |  | 1.63 | 28.9
DATE OF TEST : |  |  | 2003-11-07 |  | TIME : |  | 07:00:00 AM
[15 empty] | 10 | 0.901 | 88.1
[15 empty] | 100 | 4.57 | 85.7
[15 empty] | 1000 | 1.61 | 57.8
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 17.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 51 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1514.36 | 1516.43 |  | 1516.625 | 1519.137
Poles [20°C] |  | * | 1529.6566 | 1531.7475 |  | 1531.9444 | 1534.4818
D1 & D2 |  | * | 3061.4071 | mW |  | 3066.4323 | mW
Magnet |  |  | * | 6127.8414 | mW
|  | Poles Nr. | 02P00246 | 02P00247 |  | 02P00248 | 02P00249
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 22.3505 | 21.8173 |  | 21.0901 | 21.7035
|  | * | 22.3713 | 21.814 |  | 21.0578 | 21.8454
Capacitance |  |  | ITPstep 9d/e
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 190 | nF |  | 190 | nF
D1 & D2 | --> Masse |  | 180 | nF |  | 180 | nF
Magnet | --> Masse |  | * | 350 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 22 | 22.1 |  | 22 | 22
|  | (Q) | 0.907 | 0.901 |  | 0.908 | 0.901
D1 & D2 |  | (L) | 44 | mH |  | 44.1 | mH
|  | (Q) | 0.9 |  |  | 0.906
Magnet |  |  | (L) | 88.1 | mH
|  |  | (Q) | 0.901
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.5 | 21.5 |  | 21.5 | 21.5
|  | (Q) | 4.52 | 4.61 |  | S16 | 4.54
D1 & D2 | * | (L) | 42.9 | mH |  | 42.9 | mH
|  | (Q) | 4.57 |  |  | 4.55
Magnet | * |  | (L) | 85.7 | mH
|  |  | (Q) | 4.57
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 14.6 | 14.4 |  | 14.6 | 14.4
|  | (Q) | 1.61 | 1.64 |  | 1.63 | 1.64
D1 & D2 | * | (L) | 29 | mH |  | 28.9 | mH
|  | (Q) | 1.63 |  |  | 1.63
Magnet | * |  | (L) | 57.8 | mH
|  |  | (Q) | 1.61
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 23.8 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 25.2 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 15.3 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 11.8 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 48.8 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 38.4 | GW |  | >1000MW
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.095 | µA |  | < 20 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.186 | µA |  | < 20 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.065 | µA |  | < 20 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.09 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.041 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.027 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.975 | 0.9398 |  | 0.975 | 0.964
| Dipoles D1 & D2 [4KV] * |  | 1.69 | mS | * | 1.7 | mS
| Magnet [4KV] |  | * | 2.51 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=800V] |  |  |  | µS |  |  | µS
| [C= 2µF] | Current | OK | OK | A | OK | OK | A
Insul. Resistance All QHs --> Masse |  |  |  | 13.1 | GW |  | >1000MW
[V=1.0.KV, 60'']
Insul. Resistance All QHs ---> Magnet |  |  |  | 10.2 | GW |  | >1000MW
[V=1.0.KV, 60'']
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION