## 2081
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F462 |  |  |  | YT111 | 22.4954 | Magnet | 6.1647 | 6164.719 | 6196.9431 | 10 | 0.872 | 21.6 |  | 0.885 | 21.8
SUB CONTRACTOR : | [8 empty] | YT112 | 22.1907 | Aperture1 | 3.08 | 3079.967 | 3096.0665 | 100 | 4.66 | 21.4 |  | 4.61 | 21.5
[9 empty] | YT121 | 23.4923 | Aperture2 | 3.0847 | 3084.734 | 3100.8585 | 1000 | 1.62 | 15 |  | 1.62 | 15
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 23.5372 | Apt1 Pup | 1.5393 | 1539.322 | 1547.3683
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 2081 |  | YT211 | 21.7027 | Apt1 Plw | 1.5406 | 1540.637 | 1548.6902 | 10 | 0.868 | 21.5 |  | 0.872 | 21.7
[9 empty] | YT212 | 21.4594 | Apt2 Pup | 1.5403 | 1540.265 | 1548.3162 | 100 | 4.69 | 21.4 |  | 4.63 | 21.5
CERN INSPECTION & TEST PLAN NUMBER : 9a To 9i |  |  |  |  | TEST NUMBER : |  | 9a to 9i |  | YT221 | 22.5802 | Apt2 Plw | 1.5444 | 1544.437 | 1552.5101 | 1000 | 1.64 | 14.8 |  | 1.64 | 14.8
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 22.446
[15 empty] | 10 | 0.874 | 43.3 |  | 0.878 | 43.6
NAME OF TEST OPERATOR: |  |  | M.Levrero | [11 empty] | 100 | 4.71 | 42.8 |  | 4.64 | 42.9
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 1.63 | 29.8 |  | 1.63 | 29.8
DATE OF TEST : |  |  | 2004-02-13 |  | TIME : |  | 7:00
[15 empty] | 10 | 0.892 | 87.1
[15 empty] | 100 | 4.71 | 85.5
[15 empty] | 1000 | 1.63 | 59.6
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18.7 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 27 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1539.322 | 1540.637 |  | 1540.265 | 1544.437
Poles [20°C] |  | * | 1547.3683 | 1548.6902 |  | 1548.3162 | 1552.5101
D1 & D2 |  | * | 3096.0665 | mW |  | 3100.8585 | mW
Magnet |  |  | * | 6196.9431 | mW
|  | Poles Nr. | 02P00322 | 02P00323 |  | 02P00324 | 02P00325
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 22.4954 | 23.4923 |  | 21.7027 | 22.5802
|  | * | 22.1907 | 23.5372 |  | 21.4594 | 22.446
Capacitance |  |  | ITPstep 9d/e
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 200 | nF |  | 200 | nF
D1 & D2 | --> Masse |  | 200 | nF |  | 200 | nF
Magnet | --> Masse |  | * | 400 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.6 | 21.5 |  | 21.8 | 21.7
|  | (Q) | 0.872 | 0.868 |  | 0.885 | 0.872
D1 & D2 |  | (L) | 43.3 | mH |  | 43.6 | mH
|  | (Q) | 0.874 |  |  | 0.878
Magnet |  |  | (L) | 87.1 | mH
|  |  | (Q) | 0.892
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.4 | 21.4 |  | 21.5 | 21.5
|  | (Q) | 4.66 | 4.69 |  | S16 | 4.63
D1 & D2 | * | (L) | 42.8 | mH |  | 42.9 | mH
|  | (Q) | 4.71 |  |  | 4.64
Magnet | * |  | (L) | 85.5 | mH
|  |  | (Q) | 4.71
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 15 | 14.8 |  | 15 | 14.8
|  | (Q) | 1.62 | 1.64 |  | 1.62 | 1.64
D1 & D2 | * | (L) | 29.8 | mH |  | 29.8 | mH
|  | (Q) | 1.63 |  |  | 1.63
Magnet | * |  | (L) | 59.6 | mH
|  |  | (Q) | 1.63
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 20 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 32.6 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 17.1 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 15.5 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 75 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 65.5 | GW |  | >1000MW
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.1 | µA |  | < 20 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.1 | µA |  | < 20 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.984 | 0.975 |  | 0.984 | 0.972
| Dipoles D1 & D2 [4KV] * |  | 1.71 | mS | * | 1.71 | mS
| Magnet [4KV] |  | * | 2.54 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=850V] |  | 1179 / 1159 | 1249 / 1234 | µS | 1141 / 1176 | 1181 / 1164 | µS
| [C= 7mF] | Current | 36.6 / 36.7 | 35.2 / 35.0 | A | 38.2 / 38.6 | 36.1 / 36.4 | A
Insul. Resistance All QHs --> Masse |  |  |  | 18.2 | GW |  | >1000MW
[V=3.0.KV, 60'']
Insul. Resistance All QHs ---> Magnet |  |  |  | 9.65 | GW |  | >1000MW
[V=3.0.KV, 60'']
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION