## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[9 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[9 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER : F302 |  |  | YT111 | 20.5495 | Magnet | 6.1671 | 6167.131 | 6118.1855 | 10 | 0.536 | 13.5 |  | 0.539 | 13.5
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  | YT112 | 20.9022 | Aperture1 | 3.0891 | 3089.138 | 3064.621 | 100 | 3.7 | 13.3 |  | 3.72 | 13.3
[8 empty] | YT121 | 20.7512 | Aperture2 | 3.078 | 3077.976 | 3077.976 | 1000 | 2.3 | 10.4 |  | 2.32 | 10.4
COMPONENT NAME : |  |  | Collared Coils |  |  |  |  | YT122 | 21.0443 | Apt1 Pup | 1.5433 | 1543.35 | 1531.1012
CERN PART NUMBER : |  |  | HCMB__A001 |  | Serial Number : |  | 2 | YT211 | 20.5892 | Apt1 Plw | 1.5458 | 1545.773 | 1533.505 | 10 | 0.542 | 13.5 |  | 0.542 | 13.5
[8 empty] | YT212 | 20.8992 | Apt2 Pup | 1.539 | 1539.027 | 1526.8125 | 100 | 3.71 | 13.3 |  | 3.71 | 13.3
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 16 to 18 |  | TEST NUMBER : |  | 16 to 18 | YT221 | 20.4744 | Apt2 Plw | 1.5389 | 1538.932 | 1526.7183 | 1000 | 2.33 | 10.3 |  | 2.33 | 10.3
NON CONFORMITY: |  |  | Yes/No |  | NON CONFORMITY: |  | Number | YT222 | 20.8281
[14 empty] | 10 | 0.806 | 40.8 |  | 0.796 | 40.9
NAME OF TEST OPERATOR: |  |  | Angelo Pavese | [10 empty] | 100 | 4.62 | 40.1 |  | 4.6 | 40.1
NAME OF RESPONSIBLE: |  |  | Bruno Caserza | [10 empty] | 1000 | 1.95 | 29.9 |  | 1.96 | 29.9
DATE OF TEST : |  |  | 2001-05-14 |  | TIME : |  | 17.3
[14 empty] | 10 | 0.864 | 87.3
[14 empty] | 100 | 4.72 | 85.6
[14 empty] | 1000 | 1.8 | 62.4
Controle Chez Ansaldo
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 22 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 55 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1543.35 | 1545.773 |  | 1539.027 | 1538.932
Poles [20°C] |  | * | 1531.1012 | 1533.505 |  | 1526.8125 | 1526.7183
D1 & D2 |  | * | 3064.621 | mW |  | 3077.976 | mW
Magnet |  |  | * | 6118.1855 | mW
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.5495 | 20.7512 |  | 20.5892 | 20.8992
|  | * | 20.9022 | 21.0443 |  | 20.8992 | 20.4744
Capacitance
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 240 | nF |  | 220 | nF
D1 & D2 | --> Masse |  | 170 | nF |  | 170 | nF
Magnet | --> Masse |  | * | 340 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 13.5 | 13.5 |  | 13.5 | 13.5
|  | (Q) | 0.536 | 0.542 |  | 0.539 | 0.542
D1 & D2 |  | (L) | 40.8 | mH |  | 40.9 | mH
|  | (Q) | 0.806 |  |  | 0.796
Magnet |  |  | (L) | 87.3 | mH
|  |  | (Q) | 0.864
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 13.3 | 13.3 |  | 13.3 | 13.3
|  | (Q) | 3.7 | 3.71 |  | 4.62 | 3.71
D1 & D2 | * | (L) | 40.1 | mH |  | 40.1 | mH
|  | (Q) | 4.62 |  |  | 4.6
Magnet | * |  | (L) | 85.6 | mH
|  |  | (Q) | 4.72
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 10.4 | 10.3 |  | 10.4 | 10.3
|  | (Q) | 2.3 | 2.33 |  | 2.32 | 2.33
D1 & D2 | * | (L) | 29.9 | mH |  | 29.9 | mH
|  | (Q) | 1.95 |  |  | 1.96
Magnet | * |  | (L) | 62.4 | mH
|  |  | (Q) | 1.8
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 2.1 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse *
|  |  |  | 5.05 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | *
|  |  |  | 1.08 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | *
|  |  |  | 1.59 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 4.98 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 7.05 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 2.1 | µA |  | < µA 15
[V=6.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 1.2 | µA |  | < µA 15
[V=6.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.9 | µA |  | < µA 10
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.3 | µA |  | < µA 10
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < µA 10
[V=3.KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < µA 10
[V= 3KV 5']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.984 | 1 |  | 1 | 0.988
| Dipoles D1 & D2 [4KV] * |  | 1.773 | mS | * | 1.792 | mS
| Magnet [4KV] |  | * | 2.673 | mS
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION