## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO |  | CONTRACT NUMBER : F302 |  |  |  | YT111 | 20.6116 | Magnet | 6.2449 | 6244.915 | 6146.5699 | 10 | 0.861 | 21.9 |  | 0.864 | 21.8
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  |  | YT112 | 20.9622 | Aperture1 | 3.1222 | 3122.184 | 3073.0157 | 100 | 4.74 | 21.4 |  | 4.76 | 21.4
[9 empty] | YT121 | 20.8141 | Aperture2 | 3.1227 | 3122.717 | 3122.717 | 1000 | 1.8 | 15.8 |  | 1.8 | 16
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.1181 | Apt1 Pup | 1.5584 | 1558.394 | 1533.8524
CERN PART NUMBER : |  |  | HCMB_A001 |  | Serial Number : |  | 00002_V2 |  | YT211 | 20.6512 | Apt1 Plw | 1.5638 | 1563.779 | 1539.1526 | 10 | 0.859 | 21.9 |  | 0.864 | 21.8
[9 empty] | YT212 | 20.967 | Apt2 Pup | 1.5676 | 1567.601 | 1542.9144 | 100 | 4.72 | 21.4 |  | 4.74 | 21.4
CERN INSPECTION & TEST PLAN NUMBER : 16 To 18 |  |  |  |  | TEST NUMBER : |  | 16 to 18 |  | YT221 | 20.535 | Apt2 Plw | 1.5551 | 1555.105 | 1530.6152 | 1000 | 1.85 | 15.7 |  | 1.83 | 15.7
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.8946
[15 empty] | 10 | 0.859 | 43.7 |  | 0.861 | 43.7
NAME OF TEST OPERATOR: |  |  | A.Pavese | [11 empty] | 100 | 4.73 | 42.8 |  | 4.75 | 42.8
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 1.83 | 31.5 |  | 1.83 | 31.5
Cern Inspector |  |  | C. Lopez |  | TIME : |  | 0:00
DATE OF TEST : |  |  | 2001-07-24 | [11 empty] | 10 | 0.86 | 87.5
[15 empty] | 100 | 4.72 | 85.7
[15 empty] | 1000 | 1.81 | 63.1
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 24 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 55 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1558.394 | 1563.779 |  | 1567.601 | 1555.105
Poles [20°C] |  | * | 1533.8524 | 1539.1526 |  | 1542.9144 | 1530.6152
D1 & D2 |  | * | 3073.0157 | mW |  | 3122.717 | mW
Magnet |  |  | * | 6146.5699 | mW
|  | Poles Nr. | P006 | P008 |  | P005 | P007
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.6116 | 20.8141 |  | 20.6512 | 20.967
|  | * | 20.9622 | 21.1181 |  | 20.967 | 20.535
Capacitance
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 240 | nF |  | 220 | nF
D1 & D2 | --> Masse |  | 205 | nF |  | 205 | nF
Magnet | --> Masse |  | * | 410 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.9 |  | 21.8 | 21.8
|  | (Q) | 0.861 | 0.859 |  | 0.864 | 0.864
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.859 |  |  | 0.861
Magnet |  |  | (L) | 87.5 | mH
|  |  | (Q) | 0.86
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.4 | 21.4 |  | 21.4 | 21.4
|  | (Q) | 4.74 | 4.72 |  | S16 | 4.74
D1 & D2 | * | (L) | 42.8 | mH |  | 42.8 | mH
|  | (Q) | 4.73 |  |  | 4.75
Magnet | * |  | (L) | 85.7 | mH
|  |  | (Q) | 4.72
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 15.8 | 15.7 |  | 16 | 15.7
|  | (Q) | 1.8 | 1.85 |  | 1.8 | 1.83
D1 & D2 | * | (L) | 31.5 | mH |  | 31.5 | mH
|  | (Q) | 1.83 |  |  | 1.83
Magnet | * |  | (L) | 63.1 | mH
|  |  | (Q) | 1.81
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 4.68 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 4.48 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 1.14 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 1.53 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 5.4 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 7.1 | GW |  | >1000MW
[V=1.0KV, 60'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.8 | µA |  | < 15 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 1 | µA |  | < 15 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.6 | µA |  | < 10 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.2 | µA |  | < 10 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 10 µA
[V=3.KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 10 µA
[V= 3KV 5']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 1012 | 1023 |  | 1027 | 1023
| Dipoles D1 & D2 [4KV] * |  | 1.8 | mS | * | 1.79 | mS
| Magnet [4KV] |  | * | 2.66 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=800V] | t | 200 / 200 | 200 / 201 | µS | 201 / 199 | 197 / 202 | µS
| [C= 2µF] | Current | 32.5 / 31.0 | 31.5 / 31.5 | A | 32.0 / 30.5 | 29.0 / 33.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION