## M004
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F302 |  |  |  | YT111 | 20.8961 | Magnet | 6.0013 | 6001.265 | 6049.6623 | 10 | 0.9 | 21.9 |  | 0.896 | 21.8
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  |  | YT112 | 20.5642 | Aperture1 | 2.9987 | 2998.706 | 3022.8891 | 100 | 4.8 | 21.3 |  | 4.76 | 21.4
[9 empty] | YT121 | 21.5038 | Aperture2 | 3.0026 | 3002.555 | 3026.7692 | 1000 | 1.81 | 15.4 |  | 1.76 | 15.8
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.0308 | Apt1 Pup | 1.4951 | 1495.146 | 1507.2036
CERN PART NUMBER : |  |  | HCMB_A001 |  | Serial Number : |  | M004 |  | YT211 | 21.3103 | Apt1 Plw | 1.5036 | 1503.554 | 1515.6794 | 10 | 0.894 | 21.9 |  | 0.896 | 21.8
[9 empty] | YT212 | 20.92 | Apt2 Pup | 1.5007 | 1500.737 | 1512.8397 | 100 | 4.77 | 21.4 |  | 4.75 | 21.3
CERN INSPECTION & TEST PLAN NUMBER : 16 To 18 |  |  |  |  | TEST NUMBER : |  | 16 to 18 |  | YT221 | 20.5576 | Apt2 Plw | 1.5018 | 1501.816 | 1513.9274 | 1000 | 1.8 | 15.4 |  | 1.81 | 15.4
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 20.5018
[15 empty] | 10 | 0.895 | 43.7 |  | 0.895 | 43.7
NAME OF TEST OPERATOR: |  |  | A.Pavese | [11 empty] | 100 | 4.76 | 42.8 |  | 4.78 | 42.8
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 1.78 | 31.4 |  | 1.78 | 31.4
DATE OF TEST : |  |  | 2001-12-19 |  | TIME : |  | 0:00
[15 empty] | 10 | 0.894 | 87.4
[15 empty] | 100 | 4.76 | 85.6
[15 empty] | 1000 | 1.8 | 61.9
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 18 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 32 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1495.146 | 1503.554 |  | 1500.737 | 1501.816
Poles [20°C] |  | * | 1507.2036 | 1515.6794 |  | 1512.8397 | 1513.9274
D1 & D2 |  | * | 3022.8891 | mW |  | 3026.7692 | mW
Magnet |  |  | * | 6049.6623 | mW
|  | Poles Nr. | P019 | P020 |  | P014 | P021
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.8961 | 21.5038 |  | 21.3103 | 20.5576
|  | * | 20.5642 | 21.0308 |  | 20.92 | 20.5018
Capacitance
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 200 | nF |  | 190 | nF
D1 & D2 | --> Masse |  | 260 | nF |  | 320 | nF
Magnet | --> Masse |  | * | 390 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.9 |  | 21.8 | 21.8
|  | (Q) | 0.9 | 0.894 |  | 0.896 | 0.896
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.895 |  |  | 0.895
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.894
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.3 | 21.4 |  | 21.4 | 21.3
|  | (Q) | 4.8 | 4.77 |  | 4.76 | 4.75
D1 & D2 | * | (L) | 42.8 | mH |  | 42.8 | mH
|  | (Q) | 4.76 |  |  | 4.78
Magnet | * |  | (L) | 85.6 | mH
|  |  | (Q) | 4.76
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 15.4 | 15.4 |  | 15.8 | 15.4
|  | (Q) | 1.81 | 1.8 |  | 1.76 | 1.81
D1 & D2 | * | (L) | 31.4 | mH |  | 31.4 | mH
|  | (Q) | 1.78 |  |  | 1.78
Magnet | * |  | (L) | 61.9 | mH
|  |  | (Q) | 1.8
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 13.4 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 18.3 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 2.42 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 5.85 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 11.8 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 12.2 | GW |  | >1000MW
[V=1.0KV, 60'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.1 | µA |  | < 20 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.1 | µA |  | < 20 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.3 | µA |  | < 20 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0 KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V= 3.0 KV 5']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 1 | 1 |  | 0.98 | 1
| Dipoles D1 & D2 [4KV] * |  | 1.792 | mS | * | 1.792 | mS
| Magnet [4KV] |  | * | 2.673 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=800V] | t | 184 / 183 | 183 / 183 | µS | 188 / 184 | 184 / 183 | µS
| [C= 2µF] | Current | 30.0 / 30.5 | 29.5 / 30.0 | A | 32.0 / 29.5 | 30.5 / 30.0 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION