## M008
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F302 |  |  |  | YT111 | 21.1746 | Magnet | 6.0921 | 6092.083 | 6019.8449 | 10 | 0.881 | 21.8 |  | 0.879 | 21.8
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  |  | YT112 | 21.4269 | Aperture1 | 3.051 | 3051.02 | 3014.8419 | 100 | 4.74 | 21.3 |  | 4.72 | 21.3
[9 empty] | YT121 | 21.4193 | Aperture2 | 3.0411 | 3041.051 | 3004.9911 | 1000 | 1.82 | 15.6 |  | 1.81 | 15.7
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 21.1899 | Apt1 Pup | 1.5188 | 1518.794 | 1500.7846
CERN PART NUMBER : |  |  | HCMB_A001 |  | Serial Number : |  | M008 |  | YT211 | 21.4472 | Apt1 Plw | 1.5322 | 1532.211 | 1514.0425 | 10 | 0.881 | 21.8 |  | 0.881 | 21.8
[9 empty] | YT212 | 21.5494 | Apt2 Pup | 1.5202 | 1520.218 | 1502.1917 | 100 | 4.74 | 21.3 |  | 4.71 | 21.3
CERN INSPECTION & TEST PLAN NUMBER : 16 To 18 |  |  |  |  | TEST NUMBER : |  | 16 to 18 |  | YT221 | 21.2655 | Apt2 Plw | 1.5208 | 1520.761 | 1502.7283 | 1000 | 1.83 | 15.5 |  | 1.82 | 15.5
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 21.3489
[15 empty] | 10 | 0.88 | 43.7 |  | 0.88 | 43.7
NAME OF TEST OPERATOR: |  |  | A.Pavese | [11 empty] | 100 | 4.72 | 42.8 |  | 4.71 | 42.8
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 1.81 | 31.5 |  | 1.78 | 31.4
DATE OF TEST : |  |  | 2002-02-27 |  | TIME : |  | 0:00
[15 empty] | 10 | 0.88 | 87.4
[15 empty] | 100 | 4.73 | 85.5
[15 empty] | 1000 | 1.79 | 62.9
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 23 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 46 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1518.794 | 1532.211 |  | 1520.218 | 1520.761
Poles [20°C] |  | * | 1500.7846 | 1514.0425 |  | 1502.1917 | 1502.7283
D1 & D2 |  | * | 3014.8419 | mW |  | 3004.9911 | mW
Magnet |  |  | * | 6019.8449 | mW
|  | Poles Nr. | P026 | P029 |  | P028 | P027
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 21.1746 | 21.4193 |  | 21.4472 | 21.2655
|  | * | 21.4269 | 21.1899 |  | 21.5494 | 21.3489
Capacitance
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 240 | nF |  | 260 | nF
D1 & D2 | --> Masse |  | 380 | nF |  | 380 | nF
Magnet | --> Masse |  | * | 420 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.881 | 0.881 |  | 0.879 | 0.881
D1 & D2 |  | (L) | 43.7 | mH |  | 43.7 | mH
|  | (Q) | 0.88 |  |  | 0.88
Magnet |  |  | (L) | 87.4 | mH
|  |  | (Q) | 0.88
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.3 | 21.3 |  | 21.3 | 21.3
|  | (Q) | 4.74 | 4.74 |  | 4.72 | 4.71
D1 & D2 | * | (L) | 42.8 | mH |  | 42.8 | mH
|  | (Q) | 4.72 |  |  | 4.71
Magnet | * |  | (L) | 85.5 | mH
|  |  | (Q) | 4.73
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 15.6 | 15.5 |  | 15.7 | 15.5
|  | (Q) | 1.82 | 1.83 |  | 1.81 | 1.82
D1 & D2 | * | (L) | 31.5 | mH |  | 31.4 | mH
|  | (Q) | 1.81 |  |  | 1.78
Magnet | * |  | (L) | 62.9 | mH
|  |  | (Q) | 1.79
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 3.62 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 4.66 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 3.34 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 2.38 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 14.4 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 9.3 | GW |  | >1000MW
[V=1.0KV, 60'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.2 | µA |  | < 20 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.2 | µA |  | < 20 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.3 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0 KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V= 3.0 KV 5']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 1 | 1 |  | 1 | 1
| Dipoles D1 & D2 [4KV] * |  | 1.792 | mS | * | 1.792 | mS
| Magnet [4KV] |  | * | 2.673 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=800V] | t | 171 / 167 | 170 / 169 | µS | 167 / 167 | 167 / 167 | µS
| [C= 2µF] | Current | 31.0 / 29.5 | 31.5 / 30.0 | A | 29.5 / 29.5 | 29.5 / 29.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION