## CC2053
|  |  | ELECTRICAL TESTS OF DIPOLES | [8 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [6 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
MAIN CONTRACTOR : |  |  | ANSALDO SUPERCONDUTTORI s.p.a. |  | CONTRACT NUMBER : F462 |  |  |  | YT111 | 24.0541 | Magnet | 6.2283 | 6228.261 | 6166.595 | 10 | 0.874 | 21.9 |  | 0.877 | 22
SUB CONTRACTOR : | [8 empty] | YT112 | 24.6375 | Aperture1 | 3.1129 | 3112.916 | 3082.095 | 100 | 4.67 | 21.5 |  | 4.64 | 21.5
[9 empty] | YT121 | 24.082 | Aperture2 | 3.1153 | 3115.347 | 3084.502 | 1000 | 1.64 | 15.2 |  | 1.63 | 15.1
COMPONENT NAME : |  |  | Collared Coils | [5 empty] | YT122 | 24.1437 | Apt1 Pup | 1.556 | 1556.024 | 1540.6178
CERN PART NUMBER : |  |  | HCMBB_A001 |  | Serial Number : |  | 2053 |  | YT211 | 23.8174 | Apt1 Plw | 1.5569 | 1556.89 | 1541.4752 | 10 | 0.875 | 21.8 |  | 0.877 | 22
[9 empty] | YT212 | 24.4048 | Apt2 Pup | 1.5571 | 1557.127 | 1541.7099 | 100 | 4.73 | 21.5 |  | 4.62 | 21.5
CERN INSPECTION & TEST PLAN NUMBER : 9a To 9i |  |  |  |  | TEST NUMBER : |  | 9a to 9i |  | YT221 | 24.9597 | Apt2 Plw | 1.5582 | 1558.21 | 1542.7822 | 1000 | 1.65 | 14.9 |  | 1.65 | 14.9
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number |  | YT222 | 24.9156
[15 empty] | 10 | 0.878 | 43.6 |  | 0.874 | 43.7
NAME OF TEST OPERATOR: |  |  | M.Levrero | [11 empty] | 100 | 4.72 | 42.9 |  | 4.62 | 43
NAME OF RESPONSIBLE: |  |  | B.Caserza | [11 empty] | 1000 | 1.64 | 30.1 |  | 1.64 | 30.1
DATE OF TEST : |  |  | 2003-09-20 |  | TIME : |  | 10:00
[15 empty] | 10 | 0.867 | 86.9
[15 empty] | 100 | 4.71 | 85.9
[15 empty] | 1000 | 1.64 | 60.2
R[dc] of the Poles |  |  | ITP step 9a
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 22.5 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 58 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1556.024 | 1556.89 |  | 1557.127 | 1558.21
Poles [20°C] |  | * | 1540.6178 | 1541.4752 |  | 1541.7099 | 1542.7822
D1 & D2 |  | * | 3082.095 | mW |  | 3084.502 | mW
Magnet |  |  | * | 6166.595 | mW
|  | Poles Nr. | 02P00210 | 02P00211 |  | 02P00212 | 02P00213
R[dc] of the Quench Heaters |  |  | ITP step 9b
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 24.0541 | 24.082 |  | 23.8174 | 24.9597
|  | * | 24.6375 | 24.1437 |  | 24.4048 | 24.9156
Capacitance |  |  | ITPstep 9d/e
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 220 | nF |  | 230 | nF
D1 & D2 | --> Masse |  | 200 | nF |  | 200 | nF
Magnet | --> Masse |  | * | 420 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.9 | 21.8 |  | 22 | 22
|  | (Q) | 0.874 | 0.875 |  | 0.877 | 0.877
D1 & D2 |  | (L) | 43.6 | mH |  | 43.7 | mH
|  | (Q) | 0.878 |  |  | 0.874
Magnet |  |  | (L) | 86.9 | mH
|  |  | (Q) | 0.867
INDUCTANCE L/Q[100Hz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.5 | 21.5 |  | 21.5 | 21.5
|  | (Q) | 4.67 | 4.73 |  | S16 | 4.62
D1 & D2 | * | (L) | 42.9 | mH |  | 43 | mH
|  | (Q) | 4.72 |  |  | 4.62
Magnet | * |  | (L) | 85.9 | mH
|  |  | (Q) | 4.71
INDUCTANCE L/Q[1.0KHz] |  |  | ITP step 9c
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 15.2 | 14.9 |  | 15.1 | 14.9
|  | (Q) | 1.64 | 1.65 |  | 1.63 | 1.65
D1 & D2 | * | (L) | 30.1 | mH |  | 30.1 | mH
|  | (Q) | 1.64 |  |  | 1.64
Magnet | * |  | (L) | 60.2 | mH
|  |  | (Q) | 1.64
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 9.65 | GW |  | >1000MW
[V=1.0.KV, 60'']
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 10 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D1(8x) D1 |  | * | 5.05 | GW |  | >1000MW
[V=1.0.KV, 60'']
| QHs D2(8x) D2 |  | * | 3.4 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 14.7 | GW |  | >1000MW
[V=1.0.KV, 60'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 11.3 | GW |  | >1000MW
DIELECTRIC TESTS |  |  | ITP step 9f/h
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.1 | µA |  | < 20 µA
[V=5.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.1 | µA |  | < 20 µA
[V=5.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.1 | µA |  | < 20 µA
[V=3.0.KV 5' ]
DISCHARGE TEST |  |  | ITP step 9i
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.975 | 0.936 |  | 0.9756 | 0.9596
| Dipoles D1 & D2 [4KV] * |  | 1.71 | mS | * | 1.7 | mS
| Magnet [4KV] |  | * | 2.52 | mS
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=800V] |  | 203 / 199 | 201 / 203 | µS | 203 / 203 | 203 / 205 | µS
| [C= 2µF] | Current | 28.5 / 27.5 | 28.0 / 28.5 | A | 29.5 / 28.5 | 28.5 /28.5 | A
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION