## Coils-Coll.
|  |  | ELECTRICAL TESTS OF DIPOLES | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING
|  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[9 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[9 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
[8 empty] | YT111 | 20.0678 | Magnet | 6.1568 | 6156.756 | 6146.9209 | 10 | 0.878 | 21.8 |  | 0.866 | 21.6
MAIN CONTRACTOR : |  |  | NOELL |  | CONTRACT NUMBER : F303 |  |  | YT112 | 20.4463 | Aperture1 | 3.075 | 3075.006 | 3070.0938 | 100 | 4.56 | 21.3 |  | 4.55 | 21.3
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  | YT121 | 20.1837 | Aperture2 | 3.0817 | 3081.75 | 3081.75 | 1000 | 1.69 | 14.9 |  | 1.69 | 14.9
[8 empty] | YT122 | 20.3412 | Apt1 Pup | 1.5391 | 1539.111 | 1536.6524
COMPONENT NAME : |  |  | Collared Coils |  |  |  |  | YT211 | 20.1687 | Apt1 Plw | 1.5359 | 1535.886 | 1533.4325 | 10 | 0.872 | 21.6 |  | 0.88 | 21.7
CERN PART NUMBER : |  |  | HCMB__A001 |  | Serial Number : |  | 000001 | YT212 | 20.2519 | Apt2 Pup | 1.5447 | 1544.677 | 1542.2095 | 100 | 4.55 | 21.3 |  | 4.59 | 21.3
[8 empty] | YT221 | 20.3988 | Apt2 Plw | 1.5371 | 1537.067 | 1534.6116 | 1000 | 1.7 | 14.6 |  | 1.71 | 14.6
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 16 to 18 |  | TEST NUMBER : |  | 16 to 18 | YT222 | 20.4273
NON CONFORMITY: |  |  | No |  | NON CONFORMITY: |  | Number | [6 empty] | 10 | 0.881 | 43.6 |  | 0.874 | 43.2
[14 empty] | 100 | 4.57 | 42.5 |  | 4.58 | 42.6
NAME OF TEST OPERATOR: |  |  | Zehner | [10 empty] | 1000 | 1.7 | 29.5 |  | 1.7 | 29.4
NAME OF RESPONSIBLE: |  |  | Zehner
DATE OF TEST : |  |  | 2001-06-03 |  | TIME : |  | 15 | [6 empty] | 10 | 0.876 | 86.8
[14 empty] | 100 | 4.58 | 85
[14 empty] | 1000 | 1.7 | 59.1
CERN Reception [Bat.181]
R[dc] of the Poles
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int]
Temp.* : | 20.4 | °C | Upper | Lower |  | Upper | Lower
Humidite: | 34.5 | % | [mW] | [mW] |  | [mW] | [mW]
Poles |  |  | 1539.111 | 1535.886 |  | 1544.677 | 1537.067
Poles [20°C] |  | * | 1536.6524 | 1533.4325 |  | 1542.2095 | 1534.6116
D1 & D2 |  | * | 3070.0938 | mW |  | 3081.75 | mW
Magnet |  |  | * | 6146.9209 | mW
R[dc] of the Quench Heaters
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Left | Right |  | Left | Right
|  |  | [W] | [W] |  | [W] | [W]
D1 & D2 |  | * | 20.0678 | 20.1837 |  | 20.1687 | 20.2519
|  | * | 20.4463 | 20.3412 |  | 20.2519 | 20.3988
Capacitance
[ Megger 100V ; > 1'] |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
QHs | --> Dipoles |  | 200 | nF |  | 240 | nF
D1 & D2 | --> Masse |  | 200 | nF |  | 200 | nF
Magnet | --> Masse |  | * | 330 | nF
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INDUCTANCE L/Q[10Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES |  | (L) | 21.8 | 21.6 |  | 21.6 | 21.7
|  | (Q) | 0.878 | 0.872 |  | 0.866 | 0.88
D1 & D2 |  | (L) | 43.6 | mH |  | 43.2 | mH
|  | (Q) | 0.881 |  |  | 0.874
Magnet |  |  | (L) | 86.8 | mH
|  |  | (Q) | 0.876
INDUCTANCE L/Q[100Hz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 21.3 | 21.3 |  | 21.3 | 21.3
|  | (Q) | 4.56 | 4.55 |  | 4.55 | 4.59
D1 & D2 | * | (L) | 42.5 | mH |  | 42.6 | mH
|  | (Q) | 4.57 |  |  | 4.58
Magnet | * |  | (L) | 85 | mH
|  |  | (Q) | 4.58
INDUCTANCE L/Q[1.0KHz]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int]
|  |  | Upper | Lower |  | Upper | Lower
|  |  | [mH] | [mH] |  | [mH] | [mH]
POLES | * | (L) | 14.9 | 14.6 |  | 14.9 | 14.6
|  | (Q) | 1.69 | 1.7 |  | 1.69 | 1.71
D1 & D2 | * | (L) | 29.5 | mH |  | 29.4 | mH
|  | (Q) | 1.7 |  |  | 1.7
Magnet | * |  | (L) | 59.1 | mH
|  |  | (Q) | 1.7
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBE)
INSULATION RESISTANCE
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 11.5 | GW |  | >1000MW
[V=1.0.KV, 30'']
Dipole D2 + QHs D2 ----> Masse *
|  |  |  | 10.6 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D1(8x) D1 |  | *
|  |  |  | 2.56 | GW |  | >1000MW
[V=1.0.KV, 30'']
| QHs D2(8x) D2 |  | *
|  |  |  | 1.92 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 10.4 | GW |  | >1000MW
[V=1.0.KV, 30'']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 11.8 | GW |  | >1000MW
[V=1.0KV, 30'']
DIELECTRIC TESTS
Dipole D1 + QHs D1 ----> Masse * |  |  |  | 0.01 | µA
[V=6.0KV 5' ]
Dipole D2 + QHs D2 ----> Masse * |  |  |  | 0.01 | µA
[V=6.0KV 5' ]
| QHs D1(8x) D1 |  | * | 0.01 | µA
[V=3.0.KV 5' ]
| QHs D2(8x) D2 |  | * | 0.01 | µA
[V=3.0.KV 5' ]
DIPOLE 1
| POLE UP -----> POLE LW |  | * | 0.01 | µA
[V=3.KV 5']
DIPOLE 2
| POLE UP -----> POLE LW |  | * | 0.01 | µA
[V= 3KV 5']
DISCHARGE TEST
V = 100V/turn |  |  | Apt 1 | [ext] |  | Apt 2 | [int]
[C= 2µF] |  |  | Upper | Lower |  | Upper | Lower
|  |  | mS | mS |  | mS | mS
| Poles [4.0KV] | * | 0.972 | 0.972 |  | 0.968 | 0.968
| Dipoles D1 & D2 [4KV] * |  | 1.74 | mS | * | 1.74 | mS
| Magnet [4KV] |  | * | 2.62 | mS
Apt1
Apt2
Up
Lw
Dip
Magnet
LHC/MMS TRACEABILITY INFORMATION