## N-0112C
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 23.8483 | Magnet | 6.1869 | 6186.888 | 6135.3511 | 10 | 0.875 | 21.8 |  | 0.873 | 21.8
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F303 |  | YT112 | 23.4571 | Aperture1 | 3.0936 | 3093.588 | 3067.8183 | 100 | 4.59 | 21.3 |  | 4.59 | 21.3
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ---- |  | YT121 | 24.2503 | Aperture2 | 3.0935 | 3093.483 | 3067.7142 | 1000 | 1.73 | 15.4 |  | 1.74 | 15.3
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 24.1918 | Apt1 Pup | 1.547 | 1546.988 | 1534.1015
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-0112C |  | YT211 | 23.494 | Apt1 Plw | 1.5467 | 1546.705 | 1533.8209 | 10 | 0.874 | 21.8 |  | 0.875 | 21.8
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 10 |  | YT212 | 23.658 | Apt2 Pup | 1.5473 | 1547.258 | 1534.3693 | 100 | 4.6 | 21.3 |  | 4.6 | 21.3
BNN DOC ID NUMBER : |  |  | CF0037_C__N-0112C |  | BNN ORDER NUMBER : |  | 91300 |  | YT221 | 23.8444 | Apt2 Plw | 1.5463 | 1546.336 | 1533.455 | 1000 | 1.75 | 15 |  | 1.76 | 15
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 24.3262
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.863 | 43.6 |  | 0.863 | 43.5
[15 empty] | 100 | 4.56 | 42.6 |  | 4.56 | 42.6
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.76 | 30.5 |  | 1.78 | 30.3
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 2003-04-22 |  | TIME : |  | ----- | [7 empty] | 10 | 0.857 | 87.1
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$N-0112C |  |  | DATE OF REPORT : |  | 2003-04-23 | [7 empty] | 100 | 4.54 | 85.3
[15 empty] | 1000 | 1.76 | 61.1
| R[dc] of the POLES |  | Date of Test: | 2003-04-23 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 22.1 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 30.9 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1546.988 | 1546.705 |  | 1547.258 | 1546.336
Poles | [20°C] | * | 1534.1015 | 1533.8209 |  | 1534.3693 | 1533.455
|  |  | N-0145P | N-0146P |  | N-0147P | N-0148P
D1 & D2 | [20°C] | * | 3067.8183 | mW |  | 3067.7142 | mW
Magnet | [20°C] |  | * | 6135.3511 | mW | SIGN: | Mehler
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 2003-04-22 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 23.8483 | 24.2503 |  | 23.494 | 23.8444
SIGN: | Mehler | * | 23.4571 | 24.1918 |  | 23.658 | 24.3262
| CAPACITANCE |  | Date of Test: | 2003-04-22 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 190 | nF |  | 190 | nF
9d
D1 & D2 | ----> Masse |  | 160 | nF |  | 160 | nF
Magnet | ----> Masse |  | * | 320 | nF | SIGN: | Mehler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 2003-04-22 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00125]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.8
|  | (Q) | 0.875 | 0.874 |  | 0.873 | 0.875
|  |  | N-0145P | N-0146P |  | N-0147P | N-0148P
D1 & D2 |  | (L) | 43.6 | mH |  | 43.5 | mH
|  | (Q) | 0.863 |  |  | 0.863
Magnet |  |  | (L) | 87.1 | mH
|  |  | (Q) | 0.857 |  | SIGN: | Mehler
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 2003-04-22 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00125]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 21.3 | 21.3 |  | 21.3 | 21.3
|  | (Q) | 4.59 | 4.6 |  | 4.59 | 4.6
|  |  | N-0145P | N-0146P |  | N-0147P | N-0148P
D1 & D2 | * | (L) | 42.6 | mH |  | 42.6 | mH
|  | (Q) | 4.56 |  |  | 4.56
Magnet | * |  | (L) | 85.3 | mH
|  |  | (Q) | 4.54 |  | SIGN: | Mehler
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: |  | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00125]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 15.4 | 15 |  | 15.3 | 15
|  | (Q) | 1.73 | 1.75 |  | 1.74 | 1.76
|  |  | N-0145P | N-0146P |  | N-0147P | N-0148P
D1 & D2 | * | (L) | 30.5 | mH |  | 30.3 | mH
|  | (Q) | 1.76 |  |  | 1.78
Magnet | * |  | (L) | 61.1 | mH
|  |  | (Q) | 1.76 |  | SIGN: | Mehler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 2003-04-22 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 25.2 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 23 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 12.4 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 10.3 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 39.4 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 35.4 | GW |  | >1000MW
[5 empty] | SIGN: | Mehler
| DIELECTRIC TESTS |  | Date of Test: | 2003-04-22 | Equipment: | Breakdown Tester BT1201 [BM 00121]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.9 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.9 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.8 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.7 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.6 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.7 | µA |  | <10µA
[5 empty] | SIGN: | Mehler
| DISCHARGE TEST |  | Date of Test: | 2003-04-23 | Equipment: | Seitz Impulse Tester [BM 00296]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 0.956 | 0.956 |  | 0.956 | 0.96
| Dipoles D1 & D2 [4KV] | * | 1.71 | msec |  | 1.7 | * | 9l
| Magnet [4KV] |  |  | 2.55 | *msec | SIGN: | Mehler
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  | 400 | 364 | µsec | 400 | 400 | µsec
SIGN: | Mehler | Current | 31.5 | 30.5 | A | 31 | 30 | A
|  | test by |  | supervisor |  | approval
name |  | Mehler |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 2003-04-23 |  | 2003-04-23 |  | 2003-04-23
signature
Note on H11: Bei einer Wiederholungs-messung ist der Revisions-buchstabe (z.B. A) direkt an die BNN SERIAL NUMBER anzuhängen, z.B. N-0245CA)!
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0