## Coils-Coll.
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 23.0274 | Magnet | 6.2398 | 6239.84 | 6107.9092 | 10 | 0.891 | 22.1 |  | 0.897 | 22.1
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F303 |  | YT112 | 21.5869 | Aperture1 | 3.1188 | 3118.77 | 3052.8289 | 100 | 4.5 | 21.3 |  | 4.53 | 21.3
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  |  | YT121 | 21.0085 | Aperture2 | 3.121 | 3121.007 | 3055.0186 | 1000 | 1.67 | 15.1 |  | 1.66 | 15
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 21.9197 | Apt1 Pup | 1.5593 | 1559.332 | 1526.3626
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-0113C |  | YT211 | 20.8858 | Apt1 Plw | 1.5595 | 1559.467 | 1526.4947 | 10 | 0.9 | 22.2 |  | 0.89 | 22.1
CERN PART NUMBER : |  |  | HCMB__A001 |  | Serial Number : |  | 000011 |  | YT212 | 21.2915 | Apt2 Pup | 1.5578 | 1557.805 | 1524.8679 | 100 | 4.54 | 21.3 |  | 4.54 | 21.3
BNN DOC ID NUMBER : |  |  | QC0042_A |  | BNN ORDER NUMBER : |  | 91300 |  | YT221 | 21.552 | Apt2 Plw | 1.5633 | 1563.295 | 1530.2418 | 1000 | 1.66 | 14.7 |  | 1.64 | 14.7
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 21.155
NON CONFORMITY : |  |  | No |  | NON CONFORMITY: | [9 empty] | 10 | 0.877 | 43.8 |  | 0.873 | 43.8
[15 empty] | 100 | 4.54 | 42.5 |  | 4.52 | 42.5
NAME OF TEST OPERATOR : |  |  | Moresi |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.64 | 29.7 |  | 1.65 | 29.7
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 2002-07-31 |  | TIME : |  | 15 | [7 empty] | 10 | 0.871 | 87.1
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$Coils-Coll. |  |  | DATE OF REPORT : |  | 2002-08-01 | [7 empty] | 100 | 4.51 | 84.9
[15 empty] | 1000 | 1.64 | 59.3
| R[dc] of the POLES |  | Date of Test: | 2002-07-31 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 25.4 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 50 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
POLES |  |  | 1559.332 | 1559.467 |  | 1557.805 | 1563.295
POLES | [20°C] | * | 1526.3626 | 1526.4947 |  | 1524.8679 | 1530.2418
|  |  | N-0149P | N-0150P |  | N-0151P | N-0153P
D1 & D2 | [20°C] | * | 3052.8289 | mW |  | 3055.0186 | mW
MAGNET | [20°C] |  | * | 6107.9092 | mW | SIGN:
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 2002-08-01 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 23.0274 | 21.0085 |  | 20.8858 | 21.2915
SIGN: |  | * | 21.5869 | 21.9197 |  | 21.2915 | 21.552
| CAPACITANCE |  | Date of Test: | 2002-07-31 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 210 | nF |  | 210 | nF
9d
D1 & D2 | ----> Masse |  | 170 | nF |  | 170 | nF
Magnet | ----> Masse |  | * | 340 | nF | SIGN:
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 2002-07-31 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
POLES |  | (L) | 22.1 | 22.2 |  | 22.1 | 22.1
|  | (Q) | 0.891 | 0.9 |  | 0.897 | 0.89
|  |  | N-0149P | N-0150P |  | N-0151P | N-0153P
D1 & D2 |  | (L) | 43.8 | mH |  | 43.8 | mH
|  | (Q) | 0.877 |  |  | 0.873
Magnet |  |  | (L) | 87.1 | mH
|  |  | (Q) | 0.871 |  | SIGN:
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 2002-07-31 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
POLES | * | (L) | 21.3 | 21.3 |  | 21.3 | 21.3
|  | (Q) | 4.5 | 4.54 |  | 4.53 | 4.54
|  |  | N-0149P | N-0150P |  | N-0151P | N-0153P
D1 & D2 | * | (L) | 42.5 | mH |  | 42.5 | mH
|  | (Q) | 4.54 |  |  | 4.52
Magnet | * |  | (L) | 84.9 | mH
|  |  | (Q) | 4.51 |  | SIGN:
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 2002-07-31 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
POLES | * | (L) | 15.1 | 14.7 |  | 15 | 14.7
|  | (Q) | 1.67 | 1.66 |  | 1.66 | 1.64
|  |  | N-0149P | N-0150P |  | N-0151P | N-0153P
D1 & D2 | * | (L) | 29.7 | mH |  | 29.7 | mH
|  | (Q) | 1.64 |  |  | 1.65
Magnet | * |  | (L) | 59.3 | mH
|  |  | (Q) | 1.64 |  | SIGN:
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 2002-08-01 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Masse * |  | 4.84 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Masse * |  | 4 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 1.49 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 1.77 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| POLE UP | ----> POLE LW * |  | 9.55 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| POLE UP | ----> POLE LW * |  | 8.1 | GW |  | >1000MW
SIGN:
| DIELECTRIC TESTS |  | Date of Test: | 2002-08-01 | Equipment: | Breakdown Tester BT1201 [BM 00121]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Masse * |  | 0.4 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Masse * |  | 1.3 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.4 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.4 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| POLE UP | ----> POLE LW * |  | 0.6 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| POLE UP | ----> POLE LW * |  | 0.6 | µA |  | <10µA
SIGN:
| DISCHARGE TEST |  | Date of Test: | 2002-07-31 | Equipment: | Seitz Impulse Tester [BM 00119]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4KV] | * | 0.996 | 0.996 |  | 0.996 | 0.996
| Dipoles D1 & D2 [4KV] | * | 1.79 | msec | * | 1.79 |  | 9l
| Magnet [4KV] |  | * | 2.66 | msec | SIGN:
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  | 344.8 | 332.4 | µsec | 332.4 | 330.6 | µsec
SIGN: |  | Current | 35 | 33.5 | A | 34 | 33 | A
|  | test by |  | supervisor |  | approval
name |  | Moresi |  | Zehner |  | Zehner
company |  | BNN |  | BNN |  | BNN
date |  | 2002-08-01 |  | 2002-08-01 |  | 2002-08-01
signature
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0