## Coils-Coll.
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data_[Logger] | [5 empty] | _RAW_Data_[Gain_Phase_Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 20.9827 | Magnet | 6.1019 | 6101.857 | 6075.1264 | 10 | 0.908 | 22.1 |  | 0.908 | 22.1
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F303 |  | YT112 | 21.0188 | Aperture1 | 3.0521 | 3052.116 | 3038.7455 | 100 | 4.52 | 21.3 |  | 4.52 | 21.3
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  |  |  | YT121 | 21.2891 | Aperture2 | 3.0497 | 3049.74 | 3036.3799 | 1000 | 1.64 | 14.9 |  | 1.66 | 15
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 21.8591 | Apt1__Pup | 1.5249 | 1524.854 | 1518.174
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-0118C |  | YT211 | 21.3162 | Apt1__Plw | 1.5273 | 1527.269 | 1520.5785 | 10 | 0.891 | 22.1 |  | 0.906 | 22.1
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 16 |  | YT212 | 20.8963 | Apt2__Pup | 1.5242 | 1524.192 | 1517.5149 | 100 | 4.51 | 21.2 |  | 4.59 | 21.3
BNN DOC ID NUMBER : |  |  | CF0037_B__N-0118C |  | BNN ORDER NUMBER : |  | 91300 |  | YT221 | 21.0425 | Apt2__Plw | 1.5256 | 1525.552 | 1518.869 | 1000 | 1.68 | 14.7 |  | 1.66 | 14.7
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 21.0759
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.879 | 43.6 |  | 0.882 | 43.8
[15 empty] | 100 | 4.52 | 42.5 |  | 4.51 | 42.4
NAME OF TEST OPERATOR : |  |  | Mehler |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.65 | 29.5 |  | 1.67 | 29.7
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 2002-12-17 |  | TIME : | [9 empty] | 10 | 0.873 | 87.1
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$Coils-Coll. |  |  | DATE OF REPORT : | [9 empty] | 100 | 4.5 | 84.8
[15 empty] | 1000 | 1.67 | 59.4
| R[dc] of the POLES |  | Date of Test: | 2002-12-17 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 21.1 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 28 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1524.854 | 1527.269 |  | 1524.192 | 1525.552
Poles | [20°C] | * | 1518.174 | 1520.5785 |  | 1517.5149 | 1518.869
|  |  | N-0170P | N-0171P |  | N-0172P | N-0173P
D1 & D2 | [20°C] | * | 3038.7455 | mW |  | 3036.3799 | mW
Magnet | [20°C] |  | * | 6075.1264 | mW | SIGN:
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 2002-12-17 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 20.9827 | 21.2891 |  | 21.3162 | 20.8963
SIGN: |  | * | 21.0188 | 21.8591 |  | 20.8963 | 21.0425
| CAPACITANCE |  | Date of Test: | 2002-12-17 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 210 | nF |  | 210 | nF
9d
D1 & D2 | ----> Masse |  | 170 | nF |  | 170 | nF
Magnet | ----> Masse |  | * | 330 | nF | SIGN:
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 2002-12-17 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 22.1 | 22.1 |  | 22.1 | 22.1
|  | (Q) | 0.908 | 0.891 |  | 0.908 | 0.906
|  |  | N-0170P | N-0171P |  | N-0172P | N-0173P
D1 & D2 |  | (L) | 43.6 | mH |  | 43.8 | mH
|  | (Q) | 0.879 |  |  | 0.882
Magnet |  |  | (L) | 87.1 | mH
|  |  | (Q) | 0.873 |  | SIGN:
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 2002-12-17 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 21.3 | 21.2 |  | 21.3 | 21.3
|  | (Q) | 4.52 | 4.51 |  | 4.52 | 4.59
|  |  | N-0170P | N-0171P |  | N-0172P | N-0173P
D1 & D2 | * | (L) | 42.5 | mH |  | 42.4 | mH
|  | (Q) | 4.52 |  |  | 4.51
Magnet | * |  | (L) | 84.8 | mH
|  |  | (Q) | 4.5 |  | SIGN:
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 2002-12-17 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 14.9 | 14.7 |  | 15 | 14.7
|  | (Q) | 1.64 | 1.68 |  | 1.66 | 1.66
|  |  | N-0170P | N-0171P |  | N-0172P | N-0173P
D1 & D2 | * | (L) | 29.5 | mH |  | 29.7 | mH
|  | (Q) | 1.65 |  |  | 1.67
Magnet | * |  | (L) | 59.4 | mH
|  |  | (Q) | 1.67 |  | SIGN:
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 2002-12-17 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 8.25 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 10.9 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 2.18 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 3.28 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 11.5 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 16.4 | GW |  | >1000MW
SIGN:
| DIELECTRIC TESTS |  | Date of Test: | 2002-12-17 | Equipment: | Breakdown Tester BT1201 [BM 00121]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.6 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.1 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.5 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.6 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.8 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.8 | µA |  | <10µA
SIGN:
| DISCHARGE TEST |  | Date of Test: | 2002-12-17 | Equipment: | Seitz Impulse Tester [BM 00119]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 1 | 0.996 |  | 0.996 | 0.996
| Dipoles D1 & D2 [4KV] | * | 1.79 | msec | * | 1.79 |  | 9l
| Magnet [4KV] |  | * | 2.66 | msec | SIGN:
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  | 331.6 | 335.4 | µsec | 335 | 336 | µsec
SIGN: |  | Current | 39 | 36 | A | 35 | 38 | A
|  | test by |  | supervisor |  | approval
name |  | Mehler/Ortega |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 2002-12-17 |  | 2003-01-09 |  | 2003-01-09
signature
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0