## Coils-Coll.
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 23.8034 | Magnet | 6.1679 | 6167.851 | 6099.5362 | 10 | 0.909 | 22.2 |  | 0.905 | 22.2
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F303 |  | YT112 | 23.8892 | Aperture1 | 3.0848 | 3084.842 | 3050.6744 | 100 | 4.52 | 21.3 |  | 4.54 | 21.3
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ---- |  | YT121 | 23.6374 | Aperture2 | 3.0831 | 3083.078 | 3048.93 | 1000 | 1.66 | 15 |  | 1.67 | 15
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 23.5955 | Apt1 Pup | 1.5421 | 1542.081 | 1525.001
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-0129C |  | YT211 | 23.6209 | Apt1 Plw | 1.5428 | 1542.82 | 1525.7318 | 10 | 0.902 | 22.1 |  | 0.908 | 22.2
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 27 |  | YT212 | 23.6987 | Apt2 Pup | 1.5413 | 1541.336 | 1524.2642 | 100 | 4.57 | 21.3 |  | 4.57 | 21.3
BNN DOC ID NUMBER : |  |  | CF0037_C__N-0129C |  | BNN ORDER NUMBER : |  | 91300 |  | YT221 | 24.0501 | Apt2 Plw | 1.5418 | 1541.816 | 1524.7389 | 1000 | 1.7 | 14.7 |  | 1.69 | 14.7
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 24.0552
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.891 | 43.7 |  | 0.892 | 43.9
[15 empty] | 100 | 4.56 | 42.5 |  | 4.56 | 42.5
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.71 | 29.9 |  | 1.68 | 29.7
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 2003-04-02 |  | TIME : |  | ----- | [7 empty] | 10 | 0.881 | 87.3
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$Coils-Coll. |  |  | DATE OF REPORT : |  | 2003-04-02 | [7 empty] | 100 | 4.54 | 85
[15 empty] | 1000 | 1.68 | 59.6
| R[dc] of the POLES |  | Date of Test: | 2003-04-02 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 22.8 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 34.9 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1542.081 | 1542.82 |  | 1541.336 | 1541.816
Poles | [20°C] | * | 1525.001 | 1525.7318 |  | 1524.2642 | 1524.7389
|  |  | N-0214P | N-0215P |  | N-0216P | N-0217P
D1 & D2 | [20°C] | * | 3050.6744 | mW |  | 3048.93 | mW
Magnet | [20°C] |  | * | 6099.5362 | mW | SIGN: | Mehler
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 2003-04-02 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 23.8034 | 23.6374 |  | 23.6209 | 24.0501
SIGN: | Mehler | * | 23.8892 | 23.5955 |  | 23.6987 | 24.0552
| CAPACITANCE |  | Date of Test: | 2003-04-02 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 190 | nF |  | 180 | nF
9d
D1 & D2 | ----> Masse |  | 150 | nF |  | 150 | nF
Magnet | ----> Masse |  | * | 310 | nF | SIGN: | Mehler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 2003-04-02 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 22.2 | 22.1 |  | 22.2 | 22.2
|  | (Q) | 0.909 | 0.902 |  | 0.905 | 0.908
|  |  | N-0214P | N-0215P |  | N-0216P | N-0217P
D1 & D2 |  | (L) | 43.7 | mH |  | 43.9 | mH
|  | (Q) | 0.891 |  |  | 0.892
Magnet |  |  | (L) | 87.3 | mH
|  |  | (Q) | 0.881 |  | SIGN: | Mehler
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 2003-04-02 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 21.3 | 21.3 |  | 21.3 | 21.3
|  | (Q) | 4.52 | 4.57 |  | 4.54 | 4.57
|  |  | N-0214P | N-0215P |  | N-0216P | N-0217P
D1 & D2 | * | (L) | 42.5 | mH |  | 42.5 | mH
|  | (Q) | 4.56 |  |  | 4.56
Magnet | * |  | (L) | 85 | mH
|  |  | (Q) | 4.54 |  | SIGN: | Mehler
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 2003-04-02 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 15 | 14.7 |  | 15 | 14.7
|  | (Q) | 1.66 | 1.7 |  | 1.67 | 1.69
|  |  | N-0214P | N-0215P |  | N-0216P | N-0217P
D1 & D2 | * | (L) | 29.9 | mH |  | 29.7 | mH
|  | (Q) | 1.71 |  |  | 1.68
Magnet | * |  | (L) | 59.6 | mH
|  |  | (Q) | 1.68 |  | SIGN: | Mehler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 2003-04-02 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 15.4 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 21.2 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 5.2 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 8.5 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 20.2 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 30.6 | GW |  | >1000MW
[5 empty] | SIGN: | Mehler
| DIELECTRIC TESTS |  | Date of Test: | 2003-04-02 | Equipment: | Breakdown Tester BT1201 [BM 00121]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.7 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.7 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.7 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.8 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.8 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.8 | µA |  | <10µA
[5 empty] | SIGN: | Mehler
| DISCHARGE TEST |  | Date of Test: | 2003-04-02 | Equipment: | Seitz Impulse Tester [BM 00219]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 0.948 | 0.948 | neuer Stossspan-nungsgenerator | 0.948 | 0.95
| Dipoles D1 & D2 [4KV] | * | 1.7 | msec |  | 1.7 | * | 9l
| Magnet [4KV] |  |  | 2.54 | *msec | SIGN: | Mehler
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  | 344 | 344 | µsec | 344 | 352 | µsec
SIGN: | Mehler | Current | 31 | 32.5 | A | 31.5 | 31.5 | A
|  | test by |  | supervisor |  | approval
name |  | Mehler |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 2003-04-02 |  | 2003-04-03 |  | 2003-04-03
signature
Note on H11: Bei einer Wiederholungs-messung ist der Revisions-buchstabe (z.B. A) direkt an die BNN SERIAL NUMBER anzuhängen, z.B. N-0245CA)!
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0