## N-0132C
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 23.9866 | Magnet | 6.1362 | 6136.191 | 6085.0764 | 10 | 0.899 | 22 |  | 0.905 | 22.1
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F303 |  | YT112 | 24.8519 | Aperture1 | 3.0674 | 3067.405 | 3041.8534 | 100 | 4.54 | 21.3 |  | 4.55 | 21.3
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ---- |  | YT121 | 24.0792 | Aperture2 | 3.0688 | 3068.801 | 3043.2378 | 1000 | 1.67 | 14.9 |  | 1.67 | 15
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 24.5655 | Apt1 Pup | 1.5339 | 1533.866 | 1521.0889
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-0132C |  | YT211 | 23.9087 | Apt1 Plw | 1.5335 | 1533.538 | 1520.7636 | 10 | 0.902 | 22.1 |  | 0.906 | 22.2
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 30 |  | YT212 | 23.8416 | Apt2 Pup | 1.5345 | 1534.46 | 1521.6779 | 100 | 4.58 | 21.3 |  | 4.54 | 21.3
BNN DOC ID NUMBER : |  |  | CF0037_C__N-0132C |  | BNN ORDER NUMBER : |  | 91300 |  | YT221 | 23.8941 | Apt2 Plw | 1.5343 | 1534.333 | 1521.552 | 1000 | 1.69 | 14.8 |  | 1.69 | 14.7
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 23.8191
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.892 | 43.9 |  | 0.891 | 43.9
[15 empty] | 100 | 4.56 | 42.5 |  | 4.57 | 42.5
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.66 | 29.4 |  | 1.69 | 29.5
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 14.04.03 |  | TIME : |  | ----- | [7 empty] | 10 | 0.882 | 87.1
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$N-0132C |  |  | DATE OF REPORT : |  | 16.04.03 | [7 empty] | 100 | 4.53 | 84.9
[15 empty] | 1000 | 1.69 | 59.5
| R[dc] of the POLES |  | Date of Test: | 15.04.03 | Equipment: | Kepco Power Supply [BM 00297], Testo 965 [BM 00116], HP34970A [BM 00295]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 22.1 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 23.9 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1533.866 | 1533.538 |  | 1534.46 | 1534.333
Poles | [20°C] | * | 1521.0889 | 1520.7636 |  | 1521.6779 | 1521.552
|  |  | N-0226P | N-0227P |  | N-0228P | N-0229P
D1 & D2 | [20°C] | * | 3041.8534 | mW |  | 3043.2378 | mW
Magnet | [20°C] |  | * | 6085.0764 | mW | SIGN: | Mehler
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 16.04.03 | Equipment: | Kepco Power Supply [BM 00297], Testo 965 [BM 00116], HP34970A [BM 00295]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 23.9866 | 24.0792 |  | 23.9087 | 23.8941
SIGN: | Mehler | * | 24.8519 | 24.5655 |  | 23.8416 | 23.8191
| CAPACITANCE |  | Date of Test: | 14.04.03 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 190 | nF |  | 200 | nF
9d
D1 & D2 | ----> Masse |  | 160 | nF |  | 160 | nF
Magnet | ----> Masse |  |  | 320 | nF | SIGN: | Mehler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 16.04.03 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 22 | 22.1 |  | 22.1 | 22.2
|  | (Q) | 0.899 | 0.902 |  | 0.905 | 0.906
|  |  | N-0226P | N-0227P |  | N-0228P | N-0229P
D1 & D2 |  | (L) | 43.9 | mH |  | 43.9 | mH
|  | (Q) | 0.892 |  |  | 0.891
Magnet |  |  | (L) | 87.1 | mH
|  |  | (Q) | 0.882 |  | SIGN: | Mehler
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 16.04.03 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 21.3 | 21.3 |  | 21.3 | 21.3
|  | (Q) | 4.54 | 4.58 |  | 4.55 | 4.54
|  |  | N-0226P | N-0227P |  | N-0228P | N-0229P
D1 & D2 | * | (L) | 42.5 | mH |  | 42.5 | mH
|  | (Q) | 4.56 |  |  | 4.57
Magnet | * |  | (L) | 84.9 | mH
|  |  | (Q) | 4.53 |  | SIGN: | Mehler
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 16.04.03 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 14.9 | 14.8 |  | 15 | 14.7
|  | (Q) | 1.67 | 1.69 |  | 1.67 | 1.69
|  |  | N-0226P | N-0227P |  | N-0228P | N-0229P
D1 & D2 | * | (L) | 29.4 | mH |  | 29.5 | mH
|  | (Q) | 1.66 |  |  | 1.69
Magnet | * |  | (L) | 59.5 | mH
|  |  | (Q) | 1.69 |  | SIGN: | Mehler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 14.04.03 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 27 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 26.8 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 11 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 11.3 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 38.2 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 39.8 | GW |  | >1000MW
[5 empty] | SIGN: | Mehler
| DIELECTRIC TESTS |  | Date of Test: | 14.04.03 | Equipment: | Breakdown Tester BT1201 [BM 00293]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.8 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.7 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.7 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.7 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.5 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.5 | µA |  | <10µA
[5 empty] | SIGN: | Mehler
| DISCHARGE TEST |  | Date of Test: | 16.04.03 | Equipment: | Seitz Impulse Tester [BM 00291]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 0.948 | 0.952 |  | 0.95 | 0.95
| Dipoles D1 & D2 [4KV] | * | 1.7 | msec |  | 1.71 | * | 9l
| Magnet [4KV] |  |  | 2.54 | *msec | SIGN: | Mehler
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  | 309 | 285 | µsec | 281 | 290 | µsec
SIGN: | Mehler | Current | 32.5 | 30.5 | A | 32 | 33 | A
|  | test by |  | supervisor |  | approval
name |  | Mehler |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 16.04.03 |  | 2003-04-17 |  | 2003-04-17
signature
Note on H11: Bei einer Wiederholungs-messung ist der Revisions-buchstabe (z.B. A) direkt an die BNN SERIAL NUMBER anzuhängen, z.B. N-0245CA)!
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0