## Coils-Coll.
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 24.8879 | Magnet | 6.128 | 6127.955 | 6084.1491 | 10 | 0.9 | 22.1 |  | 0.906 | 22.1
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F489 |  | YT112 | 25.0915 | Aperture1 | 3.0638 | 3063.77 | 3041.8685 | 100 | 3.83 | 21 |  | 3.81 | 21
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ---- |  | YT121 | 24.4495 | Aperture2 | 3.0642 | 3064.186 | 3042.2816 | 1000 | 1.12 | 10.8 |  | 1.11 | 10.9
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 24.9051 | Apt1 Pup | 1.5319 | 1531.936 | 1520.9849
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-3036C |  | YT211 | 22.7467 | Apt1 Plw | 1.5318 | 1531.835 | 1520.8846 | 10 | 0.902 | 22.1 |  | 0.903 | 22.1
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 36 |  | YT212 | 24.5739 | Apt2 Pup | 1.5317 | 1531.729 | 1520.7794 | 100 | 3.86 | 21 |  | 3.85 | 21
BNN DOC ID NUMBER : |  |  | CF0037_C__N-3036C |  | BNN ORDER NUMBER : |  | N.911004 |  | YT221 | 24.1602 | Apt2 Plw | 1.5325 | 1532.457 | 1521.5022 | 1000 | 1.14 | 10.8 |  | 1.12 | 10.7
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 24.4415
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.884 | 43.7 |  | 0.889 | 43.8
[15 empty] | 100 | 3.84 | 41.9 |  | 3.83 | 42
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.13 | 21.7 |  | 1.14 | 21.7
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 15.05.03 |  | TIME : |  | ----- | [7 empty] | 10 | 0.879 | 87.1
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$Coils-Coll. |  |  | DATE OF REPORT : |  | 2003-05-16 | [7 empty] | 100 | 3.83 | 83.8
[15 empty] | 1000 | 1.13 | 43.2
| R[dc] of the POLES |  | Date of Test: | 15.05.03 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 21.8 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 37 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1531.936 | 1531.835 |  | 1531.729 | 1532.457
Poles | [20°C] | * | 1520.9849 | 1520.8846 |  | 1520.7794 | 1521.5022
|  |  | N-3021P | N-3022P |  | N-3023P | N-3024P
D1 & D2 | [20°C] | * | 3041.8685 | mW |  | 3042.2816 | mW
Magnet | [20°C] |  | * | 6084.1491 | mW | SIGN: | Mahler
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 15.05.03 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 24.8879 | 24.4495 |  | 22.7467 | 24.1602
SIGN: | Mahler | * | 25.0915 | 24.9051 |  | 24.5739 | 24.4415
| CAPACITANCE |  | Date of Test: | 15.05.03 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 200 | nF |  | 200 | nF
9d
D1 & D2 | ----> Masse |  | 170 | nF |  | 170 | nF
Magnet | ----> Masse |  | * | 340 | nF | SIGN: | Mahler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 15.05.03 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 22.1 | 22.1 |  | 22.1 | 22.1
|  | (Q) | 0.9 | 0.902 |  | 0.906 | 0.903
|  |  | N-3021P | N-3022P |  | N-3023P | N-3024P
D1 & D2 |  | (L) | 43.7 | mH |  | 43.8 | mH
|  | (Q) | 0.884 |  |  | 0.889
Magnet |  |  | (L) | 87.1 | mH
|  |  | (Q) | 0.879 |  | SIGN: | Mahler
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 15.05.03 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 21 | 21 |  | 21 | 21
|  | (Q) | 3.83 | 3.86 |  | 3.81 | 3.85
|  |  | N-3021P | N-3022P |  | N-3023P | N-3024P
D1 & D2 | * | (L) | 41.9 | mH |  | 42 | mH
|  | (Q) | 3.84 |  |  | 3.83
Magnet | * |  | (L) | 83.8 | mH
|  |  | (Q) | 3.83 |  | SIGN: | Mahler
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 15.05.03 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 10.8 | 10.8 |  | 10.9 | 10.7
|  | (Q) | 1.12 | 1.14 |  | 1.11 | 1.12
|  |  | N-3021P | N-3022P |  | N-3023P | N-3024P
D1 & D2 | * | (L) | 21.7 | mH |  | 21.7 | mH
|  | (Q) | 1.13 |  |  | 1.14
Magnet | * |  | (L) | 43.2 | mH
|  |  | (Q) | 1.13 |  | SIGN: | Mahler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 15.05.03 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 9.9 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 14 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 6.4 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 8.95 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 23.2 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 32.8 | GW |  | >1000MW
[5 empty] | SIGN: | Mahler
| DIELECTRIC TESTS |  | Date of Test: | 15.05.03 | Equipment: | Breakdown Tester BT1201 [BM 00121]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.6 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.6 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.7 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.7 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.8 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.8 | µA |  | <10µA
[5 empty] | SIGN: | Mahler
| DISCHARGE TEST |  | Date of Test: | 2003-05-16 | Equipment: | Seitz Impulse Tester [BM 00119]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 0.94 | 0.94 |  | 0.94 | 0.94
| Dipoles D1 & D2 [4KV] | * | 1.7 | msec |  | 1.7 | * | 9l
| Magnet [4KV] |  |  | 2.54 | *msec | SIGN: | Mahler
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  | 318.2 | 304.8 | µsec | 303 | 309 | µsec
SIGN: | Mahler | Current | 28.5 | 29 | A | 33.5 | 31 | A
|  | test by |  | supervisor |  | approval
name |  | Mahler |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 2003-05-16
signature
Note on H11: Bei einer Wiederholungs-messung ist der Revisions-buchstabe (z.B. A) direkt an die BNN SERIAL NUMBER anzuhängen, z.B. N-0245CA)!
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0