## N-3048C
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 24.1132 | Magnet | 6.2279 | 6227.932 | 6125.0315 | 10 | 0.882 | 22.1 |  | 0.889 | 22.2
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F489 |  | YT112 | 24.0761 | Aperture1 | 3.1146 | 3114.575 | 3063.1147 | 100 | 3.74 | 21 |  | 3.73 | 21
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ---- |  | YT121 | 24.5398 | Aperture2 | 3.1134 | 3113.412 | 3061.9709 | 1000 | 1.1 | 10.5 |  | 1.1 | 10.6
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 24.2772 | Apt1 Pup | 1.5581 | 1558.057 | 1532.3141
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-3048C |  | YT211 | 24.787 | Apt1 Plw | 1.5566 | 1556.559 | 1530.8409 | 10 | 0.888 | 22.1 |  | 0.894 | 22.3
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 48 |  | YT212 | 24.7199 | Apt2 Pup | 1.5569 | 1556.882 | 1531.1585 | 100 | 3.75 | 21 |  | 3.77 | 21
BNN DOC ID NUMBER : |  |  | CF0037_C__N-3048C |  | BNN ORDER NUMBER : |  | N.911004 |  | YT221 | 24.9141 | Apt2 Plw | 1.5567 | 1556.653 | 1530.9333 | 1000 | 1.12 | 10.4 |  | 1.11 | 10.5
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 24.8478
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.874 | 44 |  | 0.87 | 43.9
[15 empty] | 100 | 3.74 | 41.9 |  | 3.75 | 42
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.1 | 21 |  | 1.11 | 21.1
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 07.07.03 |  | TIME : |  | ----- | [7 empty] | 10 | 0.865 | 87.3
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$N-3048C |  |  | DATE OF REPORT : |  | 08.07.03 | [7 empty] | 100 | 3.74 | 83.7
[15 empty] | 1000 | 1.11 | 41.8
| R[dc] of the POLES |  | Date of Test: | 08.07.03 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 24.2 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 41.8 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1558.057 | 1556.559 |  | 1556.882 | 1556.653
Poles | [20°C] | * | 1532.3141 | 1530.8409 |  | 1531.1585 | 1530.9333
|  |  | N-3069P | N-3070P |  | N-3071P | N-3072P
D1 & D2 | [20°C] | * | 3063.1147 | mW |  | 3061.9709 | mW
Magnet | [20°C] |  | * | 6125.0315 | mW | SIGN: | Mehler
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 07.07.03 | Equipment: | Kepco Power Supply [BM 00125], Testo 965 [BM 00116], HP34970A [BM 00122]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 24.1132 | 24.5398 |  | 24.787 | 24.9141
SIGN: | Oswald | * | 24.0761 | 24.2772 |  | 24.7199 | 24.8478
| CAPACITANCE |  | Date of Test: | 07.07.03 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 200 | nF |  | 200 | nF
9d
D1 & D2 | ----> Masse |  | 160 | nF |  | 160 | nF
Magnet | ----> Masse |  | * | 320 | nF | SIGN: | Oswald
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 07.07.03 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 22.1 | 22.1 |  | 22.2 | 22.3
|  | (Q) | 0.882 | 0.888 |  | 0.889 | 0.894
|  |  | N-3069P | N-3070P |  | N-3071P | N-3072P
D1 & D2 |  | (L) | 44 | mH |  | 43.9 | mH
|  | (Q) | 0.874 |  |  | 0.87
Magnet |  |  | (L) | 87.3 | mH
|  |  | (Q) | 0.865 |  | SIGN: | Oswald
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 07.07.03 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 21 | 21 |  | 21 | 21
|  | (Q) | 3.74 | 3.75 |  | 3.73 | 3.77
|  |  | N-3069P | N-3070P |  | N-3071P | N-3072P
D1 & D2 | * | (L) | 41.9 | mH |  | 42 | mH
|  | (Q) | 3.74 |  |  | 3.75
Magnet | * |  | (L) | 83.7 | mH
|  |  | (Q) | 3.74 |  | SIGN: | Mahler
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 07.07.03 | Equipment: | Kepco Power Supply [BM 00125], Solartron Gain Phase Analyser [BM 00124]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 10.5 | 10.4 |  | 10.6 | 10.5
|  | (Q) | 1.1 | 1.12 |  | 1.1 | 1.11
|  |  | N-3069P | N-3070P |  | N-3071P | N-3072P
D1 & D2 | * | (L) | 21 | mH |  | 21.1 | mH
|  | (Q) | 1.1 |  |  | 1.11
Magnet | * |  | (L) | 41.8 | mH
|  |  | (Q) | 1.11 |  | SIGN: | Oswald
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 07.07.03 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 20.6 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 18.8 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 7.25 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 9.6 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 23.8 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 32 | GW |  | >1000MW
[5 empty] | SIGN: | Oswald
| DIELECTRIC TESTS |  | Date of Test: | 08.07.03 | Equipment: | Breakdown Tester BT1201 [BM 00121]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.5 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.6 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.7 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.8 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.8 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.8 | µA |  | <10µA
[5 empty] | SIGN: | Mahler
| DISCHARGE TEST |  | Date of Test: | 08.07.03 | Equipment: | Seitz Impulse Tester [BM 00119]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 0.952 | 0.95 |  | 0.95 | 0.95
| Dipoles D1 & D2 [4KV] | * | 1.72 | msec |  | 1.7 | * | 9l
| Magnet [4KV] |  |  | 2.57 | *msec | SIGN: | Mahler
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  | 341 | 341 | µsec | 339 | 279.2 | µsec
SIGN: | Mahler | Current | 32.5 | 32.5 | A | 30 | 32.5 | A
|  | test by |  | supervisor |  | approval
name |  | Mahler |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 08.07.03 |  | 08.07.03 |  | 2003-07-08
signature
Note on H11: Bei einer Wiederholungs-messung ist der Revisions-buchstabe (z.B. A) direkt an die BNN SERIAL NUMBER anzuhängen, z.B. N-0245CA)!
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0