## N-3057C
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 23.7875 | Magnet | 6.2939 | 6293.856 | 6075.1506 | 10 | 0.864 | 22.1 |  | 0.858 | 22
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F489 |  | YT112 | 23.7436 | Aperture1 | 3.1476 | 3147.6 | 3038.2239 | 100 | 3.81 | 21.2 |  | 3.8 | 21.2
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ---- |  | YT121 | 23.8911 | Aperture2 | 3.1463 | 3146.257 | 3036.9276 | 1000 | 1.15 | 11.2 |  | 1.15 | 11.2
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 23.8215 | Apt1 Pup | 1.5741 | 1574.06 | 1519.3629
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-3057C |  | YT211 | 24.2832 | Apt1 Plw | 1.5735 | 1573.543 | 1518.8639 | 10 | 0.865 | 22.1 |  | 0.863 | 22.2
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 57 |  | YT212 | 24.2956 | Apt2 Pup | 1.574 | 1573.968 | 1519.2741 | 100 | 3.82 | 21.2 |  | 3.82 | 21.2
BNN DOC ID NUMBER : |  |  | CF0037_C__N-3057C |  | BNN ORDER NUMBER : |  | N.911004 |  | YT221 | 24.2404 | Apt2 Plw | 1.5723 | 1572.294 | 1517.6583 | 1000 | 1.16 | 11.1 |  | 1.16 | 11
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 24.1601
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.86 | 44.1 |  | 0.862 | 44
[15 empty] | 100 | 3.82 | 42.5 |  | 3.82 | 42.4
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.16 | 22.3 |  | 1.15 | 22.1
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 2003-07-31 |  | TIME : |  | ----- | [7 empty] | 10 | 0.859 | 87.8
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$N-3057C |  |  | DATE OF REPORT : |  | 2003-07-31 | [7 empty] | 100 | 3.79 | 84.9
[15 empty] | 1000 | 1.14 | 44.1
| R[dc] of the POLES |  | Date of Test: | 2003-07-31 | Equipment: | Kepco Power Supply [BM 297], Testo 965 [BM 00116], HP34970A [BM 295]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 29 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 37 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1574.06 | 1573.543 |  | 1573.968 | 1572.294
Poles | [20°C] | * | 1519.3629 | 1518.8639 |  | 1519.2741 | 1517.6583
|  |  | N-3105P | N-3106P |  | N-3107P | N-3108P
D1 & D2 | [20°C] | * | 3038.2239 | mW |  | 3036.9276 | mW
Magnet | [20°C] |  | * | 6075.1506 | mW | NAME: | Weinberg
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 2003-07-31 | Equipment: | Kepco Power Supply [BM 297], Testo 965 [BM 116], HP34970A [BM 295]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 23.7875 | 23.8911 |  | 24.2832 | 24.2404
NAME: | Weinberg | * | 23.7436 | 23.8215 |  | 24.2956 | 24.1601
| CAPACITANCE |  | Date of Test: | 2003-07-31 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 200 | nF |  | 200 | nF
9d
D1 & D2 | ----> Masse |  | 160 | nF |  | 160 | nF
Magnet | ----> Masse |  | * | 330 | nF | NAME: | Weinberg
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 2003-07-31 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 22.1 | 22.1 |  | 22 | 22.2
|  | (Q) | 0.864 | 0.865 |  | 0.858 | 0.863
|  |  | N-3105P | N-3106P |  | N-3107P | N-3108P
D1 & D2 |  | (L) | 44.1 | mH |  | 44 | mH
|  | (Q) | 0.86 |  |  | 0.862
Magnet |  |  | (L) | 87.8 | mH
|  |  | (Q) | 0.859 |  | NAME: | Weinberg
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 2003-07-31 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 21.2 | 21.2 |  | 21.2 | 21.2
|  | (Q) | 3.81 | 3.82 |  | 3.8 | 3.82
|  |  | N-3105P | N-3106P |  | N-3107P | N-3108P
D1 & D2 | * | (L) | 42.5 | mH |  | 42.4 | mH
|  | (Q) | 3.82 |  |  | 3.82
Magnet | * |  | (L) | 84.9 | mH
|  |  | (Q) | 3.79 |  | NAME: | Weinberg
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 2003-07-31 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 11.2 | 11.1 |  | 11.2 | 11
|  | (Q) | 1.15 | 1.16 |  | 1.15 | 1.16
|  |  | N-3105P | N-3106P |  | N-3107P | N-3108P
D1 & D2 | * | (L) | 22.3 | mH |  | 22.1 | mH
|  | (Q) | 1.16 |  |  | 1.15
Magnet | * |  | (L) | 44.1 | mH
|  |  | (Q) | 1.14 |  | NAME: | Weinberg
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 2003-07-31 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 8.9 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 6.7 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 5.65 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 6.25 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 19.3 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 20.6 | GW |  | >1000MW
[5 empty] | NAME: | Weinberg
| DIELECTRIC TESTS |  | Date of Test: | 2003-07-31 | Equipment: | Breakdown Tester BT1201 [BM 293 ]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.8 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.7 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.6 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.5 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.5 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.5 | µA |  | <10µA
[5 empty] | NAME: | Weinberg
| DISCHARGE TEST |  | Date of Test: | 2003-07-31 | Equipment: | Seitz Impulse Tester [BM 296]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 0.944 | 0.944 |  | 0.944 | 0.944
| Dipoles D1 & D2 [4KV] | * | 1.7 | msec |  | 1.7 | * | 9l
| Magnet [4KV] |  |  | 2.54 | *msec | NAME: | Weinberg
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  | 361.2 | 374.4 | µsec | 362.8 | 385.6 | µsec
NAME: | Weinberg | Current | 28.5 | 34 | A | 28 | 32.5 | A
|  | test by |  | supervisor |  | approval
name |  | Weinberg |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 2003-07-31 |  | 2003-08-05 |  | 2003-08-05
signature
Note on H11: Bei einer Wiederholungs-messung ist der Revisions-buchstabe (z.B. A) direkt an die BNN SERIAL NUMBER anzuhängen, z.B. N-0245CA)!
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0