## N-3064C
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 24.288 | Magnet | 6.2825 | 6282.484 | 6057.1577 | 10 | 0.863 | 22.1 |  | 0.864 | 22.1
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F489 |  | YT112 | 24.3641 | Aperture1 | 3.1413 | 3141.269 | 3028.6049 | 100 | 3.8 | 21.2 |  | 3.81 | 21.2
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ---- |  | YT121 | 24.2208 | Aperture2 | 3.1414 | 3141.433 | 3028.763 | 1000 | 1.15 | 11.1 |  | 1.17 | 11.3
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 24.2387 | Apt1 Pup | 1.5692 | 1569.195 | 1512.9146
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-3064C |  | YT211 | 24.1773 | Apt1 Plw | 1.5722 | 1572.244 | 1515.8542 | 10 | 0.862 | 22 |  | 0.864 | 22.1
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 64 |  | YT212 | 24.2474 | Apt2 Pup | 1.5688 | 1568.824 | 1512.5569 | 100 | 3.83 | 21.2 |  | 3.82 | 21.2
BNN DOC ID NUMBER : |  |  | CF0037_C__N-3064C |  | BNN ORDER NUMBER : |  | N.911004 |  | YT221 | 24.5413 | Apt2 Plw | 1.5728 | 1572.815 | 1516.4047 | 1000 | 1.17 | 11.1 |  | 1.18 | 11.1
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 25.0242
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.859 | 43.9 |  | 0.862 | 44
[15 empty] | 100 | 3.83 | 42.4 |  | 3.81 | 42.4
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.17 | 22.5 |  | 1.17 | 22.3
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 2003-08-21 |  | TIME : |  | ----- | [7 empty] | 10 | 0.859 | 87.7
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$N-3064C |  |  | DATE OF REPORT : |  | 2003-08-21 | [7 empty] | 100 | 3.83 | 84.8
[15 empty] | 1000 | 1.15 | 44.5
| R[dc] of the POLES |  | Date of Test: | 2003-08-21 | Equipment: | Kepco Power Supply [BM 297], Testo 965 [BM 00116], HP34970A [BM 295]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 29.3 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 33.1 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1569.195 | 1572.244 |  | 1568.824 | 1572.815
Poles | [20°C] | * | 1512.9146 | 1515.8542 |  | 1512.5569 | 1516.4047
|  |  | N-3133P | N-3134P |  | N-3135P | N-3136P
D1 & D2 | [20°C] | * | 3028.6049 | mW |  | 3028.763 | mW
Magnet | [20°C] |  | * | 6057.1577 | mW | NAME: | Oswald
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 2003-08-21 | Equipment: | Kepco Power Supply [BM 297], Testo 965 [BM 116], HP34970A [BM 295]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 24.288 | 24.2208 |  | 24.1773 | 24.5413
NAME: | Oswald | * | 24.3641 | 24.2387 |  | 24.2474 | 25.0242
| CAPACITANCE |  | Date of Test: | 2003-08-21 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 190 | nF |  | 190 | nF
9d
D1 & D2 | ----> Masse |  | 150 | nF |  | 160 | nF
Magnet | ----> Masse |  | * | 310 | nF | NAME: | Oswald
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 2003-08-21 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 22.1 | 22 |  | 22.1 | 22.1
|  | (Q) | 0.863 | 0.862 |  | 0.864 | 0.864
|  |  | N-3133P | N-3134P |  | N-3135P | N-3136P
D1 & D2 |  | (L) | 43.9 | mH |  | 44 | mH
|  | (Q) | 0.859 |  |  | 0.862
Magnet |  |  | (L) | 87.7 | mH
|  |  | (Q) | 0.859 |  | NAME: | Oswald
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 2003-08-21 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 21.2 | 21.2 |  | 21.2 | 21.2
|  | (Q) | 3.8 | 3.83 |  | 3.81 | 3.82
|  |  | N-3133P | N-3134P |  | N-3135P | N-3136P
D1 & D2 | * | (L) | 42.4 | mH |  | 42.4 | mH
|  | (Q) | 3.83 |  |  | 3.81
Magnet | * |  | (L) | 84.8 | mH
|  |  | (Q) | 3.83 |  | NAME: | Oswald
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 2003-08-21 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 11.1 | 11.1 |  | 11.3 | 11.1
|  | (Q) | 1.15 | 1.17 |  | 1.17 | 1.18
|  |  | N-3133P | N-3134P |  | N-3135P | N-3136P
D1 & D2 | * | (L) | 22.5 | mH |  | 22.3 | mH
|  | (Q) | 1.17 |  |  | 1.17
Magnet | * |  | (L) | 44.5 | mH
|  |  | (Q) | 1.15 |  | NAME: | Oswald
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 2003-08-21 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 11.5 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 16.3 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 8.1 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 8.35 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 28.2 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 25.4 | GW |  | >1000MW
[5 empty] | NAME: | Oswald
| DIELECTRIC TESTS |  | Date of Test: | 2003-08-21 | Equipment: | Breakdown Tester BT1201 [BM 293 ]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.7 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.6 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.5 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.5 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.4 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.4 | µA |  | <10µA
[5 empty] | NAME: | Oswald
| DISCHARGE TEST |  | Date of Test: | 2003-08-21 | Equipment: | Seitz Impulse Tester [BM 296]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 0.942 | 0.94 |  | 0.944 | 0.942
| Dipoles D1 & D2 [4KV] | * | 1.7 | msec |  | 1.7 | * | 9l
| Magnet [4KV] |  |  | 2.54 | *msec | NAME: | Oswald
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  | ----- | ----- | µsec | ----- | ----- | µsec
NAME: |  | Current | ----- | ----- | A | ----- | ----- | A
|  | test by |  | supervisor |  | approval
name |  | Oswald |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 2003-08-21 |  | 2003-08-22 |  | 2003-08-22
signature
Note on H11: Bei einer Wiederholungs-messung ist der Revisions-buchstabe (z.B. A) direkt an die BNN SERIAL NUMBER anzuhängen, z.B. N-0245CA)!
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0