## Coils-Coll.
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 21.2959 | Magnet | 6.2969 | 6296.93 | 6104.0423 | 10 | 0.859 | 21.8 |  | 0.866 | 21.8
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F489 |  | YT112 | 22.0245 | Aperture1 | 3.1489 | 3148.944 | 3052.4855 | 100 | 3.7 | 20.8 |  | 3.7 | 20.8
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ---- |  | YT121 | 21.4396 | Aperture2 | 3.1486 | 3148.579 | 3052.1316 | 1000 | 1.12 | 10.7 |  | 1.13 | 10.7
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 21.9861 | Apt1 Pup | 1.5743 | 1574.344 | 1526.1187
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-3243C |  | YT211 | 21.2411 | Apt1 Plw | 1.5747 | 1574.708 | 1526.4715 | 10 | 0.865 | 21.8 |  | 0.867 | 21.9
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 243 |  | YT212 | 21.9141 | Apt2 Pup | 1.5744 | 1574.414 | 1526.1865 | 100 | 3.7 | 20.8 |  | 3.67 | 20.9
BNN DOC ID NUMBER : |  |  | CF0037_D__N-3243C |  | BNN ORDER NUMBER : |  | N.911004 |  | YT221 | 21.2984 | Apt2 Plw | 1.5743 | 1574.3 | 1526.076 | 1000 | 1.14 | 10.6 |  | 1.13 | 10.6
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 22.0895
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.858 | 43.3 |  | 0.857 | 43.5
REVISION: |  |  | 0 |  | REPARATION?: |  | N | [7 empty] | 100 | 3.72 | 41.7 |  | 3.7 | 41.6
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.14 | 21.4 |  | 1.14 | 21.2
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 2004-08-19 |  | TIME : |  | ----- | [7 empty] | 10 | 0.853 | 86.5
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$Coils-Coll. |  |  | DATE OF REPORT : |  | 2004-08-19 | [7 empty] | 100 | 3.71 | 83.2
[15 empty] | 1000 | 1.13 | 42
| R[dc] of the POLES |  | Date of Test: | 2004-08-19 | Equipment: | Kepco Power Supply [BM 297], Testo 965 [BM 00116], HP34970A [BM 295]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 27.9 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 37.4 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1574.344 | 1574.708 |  | 1574.414 | 1574.3
Poles | [20°C] | * | 1526.1187 | 1526.4715 |  | 1526.1865 | 1526.076
|  |  | N-3849P | N-3850P |  | N-3851P | N-3852P
D1 & D2 | [20°C] | * | 3052.4855 | mW |  | 3052.1316 | mW
Magnet | [20°C] |  | * | 6104.0423 | mW | NAME: | Mehler
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 2004-08-19 | Equipment: | Kepco Power Supply [BM 297], Testo 965 [BM 116], HP34970A [BM 295]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 21.2959 | 21.4396 |  | 21.2411 | 21.2984
NAME: | Mehler | * | 22.0245 | 21.9861 |  | 21.9141 | 22.0895
| CAPACITANCE |  | Date of Test: | 2004-08-19 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 190 | nF |  | 190 | nF
9d
D1 & D2 | ----> Masse |  | 160 | nF |  | 160 | nF
Magnet | ----> Masse |  | * | 320 | nF | NAME: | Mehler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 2004-08-19 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 21.8 | 21.8 |  | 21.8 | 21.9
|  | (Q) | 0.859 | 0.865 |  | 0.866 | 0.867
|  |  | N-3849P | N-3850P |  | N-3851P | N-3852P
D1 & D2 |  | (L) | 43.3 | mH |  | 43.5 | mH
|  | (Q) | 0.858 |  |  | 0.857
Magnet |  |  | (L) | 86.5 | mH
|  |  | (Q) | 0.853 |  | NAME: | Heymann
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 2004-08-19 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 20.8 | 20.8 |  | 20.8 | 20.9
|  | (Q) | 3.7 | 3.7 |  | 3.7 | 3.67
|  |  | N-3849P | N-3850P |  | N-3851P | N-3852P
D1 & D2 | * | (L) | 41.7 | mH |  | 41.6 | mH
|  | (Q) | 3.72 |  |  | 3.7
Magnet | * |  | (L) | 83.2 | mH
|  |  | (Q) | 3.71 |  | NAME: | Heymann
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 2004-08-19 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 10.7 | 10.6 |  | 10.7 | 10.6
|  | (Q) | 1.12 | 1.14 |  | 1.13 | 1.13
|  |  | N-3849P | N-3850P |  | N-3851P | N-3852P
D1 & D2 | * | (L) | 21.4 | mH |  | 21.2 | mH
|  | (Q) | 1.14 |  |  | 1.14
Magnet | * |  | (L) | 42 | mH
|  |  | (Q) | 1.13 |  | NAME: | Heymann
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 2004-08-19 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 17.4 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 14.7 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 10.2 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 7.75 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 33.6 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 26 | GW |  | >1000MW
[5 empty] | NAME: | Mehler
| DIELECTRIC TESTS |  | Date of Test: | 2004-08-19 | Equipment: | Breakdown Tester BT1201 [BM 293 ]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.8 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.7 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 0.6 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 0.7 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.6 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.5 | µA |  | <10µA
[5 empty] | NAME: | Mehler
| DISCHARGE TEST |  | Date of Test: | 2004-08-19 | Equipment: | Seitz Impulse Tester [BM 296]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 0.938 | 0.938 |  | 0.938 | 0.938
| Dipoles D1 & D2 [4KV] | * | 1.7 | msec |  | 1.7 | * | 9l
| Magnet [4KV] |  |  | 2.54 | *msec | NAME: | Heymann
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  |  |  | µsec |  |  | µsec
NAME: |  | Current |  |  | A |  |  | A
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| DIQH TEST |  | Date of Test: | 2004-08-19 | Equipment: | DIGH equipment, Megger BM21 [BM138]
R[dc] Resistance
|  | YT111 / 112 | YT121 / 122 |  | YT211 / 212 | YT221 / 222
| R[dc] 4w | 21.3 | 21.4 | [W] | 21.3 | 21.2 | [W]
| R[dc] 4w | 22 | 21.9 | [W] | 22 | 22.1 | [W]
[6 empty] | NAME: | Heymann
Insulation Resistance
[5 empty] | [V = 3.0KV; 1'] |  | >1000MW
| QHs -> Ground | 24.8 |  | [GW] | 18 |  | [GW]
| QH -> Pol | 15.2 |  | [GW] | 11.3 |  | [GW]
[V = 3.0KV; 30'']
| Strip -> Strip | 43.4 | 43.2 | [GW] | 34.6 | 33.4 | [GW]
[6 empty] | NAME: | Heymann
| Discharge 850V 2.5kJ | Note: Before using 850V the QH's have to be measured with 450V! / Bemerkung: erst mit 450V messen, danach mit 850V!
|  | I [A] | t [ms] |  |  | I [A] | t [ms]
| YT111 | 38.7 | 145 |  | YT211 | 38.8 | 145
| YT112 | 37.9 | 150 |  | YT212 | 38.1 | 149
| YT121 | 38.5 | 146 |  | YT221 | 38.9 | 145
| YT122 | 38.1 | 149 |  | YT222 | 37.9 | 151
[6 empty] | NAME: | Heymann
Insulation Resistance
[5 empty] | [V = 3.0KV; 1'] |  | >1000MW
| QHs -> Ground | 28.2 |  | [GW] | 22.8 |  | [GW]
| QH -> Pol | 17.2 |  | [GW] | 12.8 |  | [GW]
[V = 3.0KV; 30'']
| Strip -> Strip | 44.8 | 43.4 | [GW] | 38.6 | 34.6 | [GW]
[6 empty] | NAME: | Heymann
R[dc] Resistance
|  | YT111 / 112 | YT121 / 122 |  | YT211 / 212 | YT221 / 222
| R[dc] 4w | 21.3 | 21.4 | [W] | 21.3 | 21.2 | [W]
| R[dc] 4w | 22.1 | 21.9 | [W] | 21.9 | 22.1 | [W]
[6 empty] | NAME: | Heymann
|  | 0 |  |  | 0
|  | 0 |  |  | 0
|  | 0 | 0 |  | 0 | 0
|  | 0 | 0 |  | 0 | 0
|  | 0 | 0 |  |  | 0
0
|  | test by |  | supervisor |  | approval
name |  | Heymann |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 2004-08-19 |  | 2004-08-23 |  | 2004-08-23
signature
Note on C241: Formel für zu stark voneinander abweichende Isolationswerte an D1(QH -> Masse)
Note on C242: Formel für zu stark voneinander abweichende Isolationswerte an D1 (QH -> Pol)
Note on C243: Formel für zu stark voneinander abweichende Isolationswerte an D1 (Strip -> Strip)
Note on C244: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on C245: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on D16: 0 für die erste Messung, A für die 1. Wiederholung, B für die 2. Wiederholung, etc.
Note on D243: Formel für zu stark voneinander abweichende Isolationswerte an D1 (Strip -> Strip)
Note on D244: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on D245: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on F241: Formel für zu stark voneinander abweichende Isolationswerte an D1(QH -> Masse)
Note on F242: Formel für zu stark voneinander abweichende Isolationswerte an D1 (QH -> Pol)
Note on F243: Formel für zu stark voneinander abweichende Isolationswerte an D1 (Strip -> Strip)
Note on F244: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on F245: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on G243: Formel für zu stark voneinander abweichende Isolationswerte an D1 (Strip -> Strip)
Note on G244: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on G245: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on H16: Y, wenn die Messung nach einer Reparatur durchgeführt wurde, N, wenn vor dieser Messung keine Reparatur durchgeführt wurde
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0