## Coils-Coll.
|  |  |  | ELECTRICAL TESTS OF DIPOLES / Collared Coil | [7 empty] | RAW_Data [Logger] | [5 empty] | RAW_Data [Gain Phase Analyser]
AFTER COLLARING / Nach dem Collarn
|  |  |  | (WITH BEAM TUBES) | [5 empty] | [DataQHs_Cl] |  | [DataPoles_Cl]
[10 empty] | QHs |  | Poles | Poles | Poles | f | Q | L |  | Q | L
[10 empty] | [W] |  | [V] | [mW] | R20[mW] | [Hz] |  | [mH] |  |  | [mH]
|  |  |  | LHC/MMS TRACEABILITY INFORMATION |  |  |  |  | YT111 | 22.063 | Magnet | 6.1507 | 6150.691 | 6030.0892 | 10 | 0.875 | 21.7 |  | 0.889 | 21.8
MAIN CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | F489 |  | YT112 | 21.6567 | Aperture1 | 3.0753 | 3075.312 | 3015.0118 | 100 | 3.78 | 20.9 |  | 3.77 | 20.9
SUB CONTRACTOR : |  |  |  |  | CONTRACT NUMBER : |  | ---- |  | YT121 | 21.9838 | Aperture2 | 3.0754 | 3075.392 | 3015.0902 | 1000 | 1.12 | 10.7 |  | 1.12 | 10.6
[5 empty] | SPECIFICATION: |  |  | LHC-MMS/98-198 Rev. 2.0 | YT122 | 21.4479 | Apt1 Pup | 1.5369 | 1536.896 | 1506.7608
COMPONENT NAME : |  |  | Collared Coils |  | BNN SERIAL NUMBER : |  | N-3252C |  | YT211 | 21.847 | Apt1 Plw | 1.5384 | 1538.421 | 1508.2559 | 10 | 0.88 | 21.9 |  | 0.894 | 21.9
CERN PART NUMBER : |  |  | HCMB__A001 |  | SERIAL NUMBER : |  | 252 |  | YT212 | 21.6496 | Apt2 Pup | 1.5372 | 1537.239 | 1507.0971 | 100 | 3.76 | 20.8 |  | 3.75 | 20.9
BNN DOC ID NUMBER : |  |  | CF0037_D__N-3252C |  | BNN ORDER NUMBER : |  | N.911004 |  | YT221 | 22.0937 | Apt2 Plw | 1.5382 | 1538.169 | 1508.0088 | 1000 | 1.16 | 10.7 |  | 1.16 | 10.7
CERN INSPECTION & TEST PLAN NUMBER : |  |  | ITP Step 9a to 9l |  | TEST NUMBER : |  | 9 |  | YT222 | 21.3922
NON CONFORMITY : |  |  | <No> |  | NON CONFORMITY REPORT : | [9 empty] | 10 | 0.876 | 43.2 |  | 0.88 | 43.4
REVISION: |  |  | 0 |  | REPARATION?: |  | N | [7 empty] | 100 | 3.77 | 41.6 |  | 3.79 | 41.7
NAME OF TEST OPERATOR : |  |  | see ITP steps |  | WORKING PLACE : |  | ON CC MOUNTING TABLE | [7 empty] | 1000 | 1.15 | 21.3 |  | 1.14 | 21.3
NAME OF RESPONSIBLE : |  |  | Zehner |  | BBP-SDA-CODE : |  | -----
DATE OF TEST : |  | (Starting) | 2004-09-01 |  | TIME : |  | ----- | [7 empty] | 10 | 0.881 | 86.5
BNN INT. REG. NO : |  | 'file:///tmp/in/input.xls'#$Coils-Coll. |  |  | DATE OF REPORT : |  | 2004-09-01 | [7 empty] | 100 | 3.78 | 83.3
[15 empty] | 1000 | 1.15 | 43.2
| R[dc] of the POLES |  | Date of Test: | 2004-09-01 | Equipment: | Kepco Power Supply [BM 297], Testo 965 [BM 00116], HP34970A [BM 295]
I = | 1 | A | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
Temp.* : | 25 | °C | Upper | Lower |  | Upper | Lower | step
Humidite: | 35.6 | % | [mW] | [mW] |  | [mW] | [mW] | 9a
Poles |  |  | 1536.896 | 1538.421 |  | 1537.239 | 1538.169
Poles | [20°C] | * | 1506.7608 | 1508.2559 |  | 1507.0971 | 1508.0088
|  |  | N-3885P | N-3886P |  | N-3887P | N-3888P
D1 & D2 | [20°C] | * | 3015.0118 | mW |  | 3015.0902 | mW
Magnet | [20°C] |  | * | 6030.0892 | mW | NAME: | Mehler
| R[dc] of the QUENCH HEATERS |  | Date of Test: | 2004-09-01 | Equipment: | Kepco Power Supply [BM 297], Testo 965 [BM 116], HP34970A [BM 295]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Left | Right |  | Left | Right | step
D1 & D2 |  |  | [W] | [W] |  | [W] | [W] | 9b
|  | * | 22.063 | 21.9838 |  | 21.847 | 22.0937
NAME: | Mehler | * | 21.6567 | 21.4479 |  | 21.6496 | 21.3922
| CAPACITANCE |  | Date of Test: | 2004-09-01 | Equipment: | Megger BM21 [BM 00138]
| [V = 500V; > 1'] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
9e
QHs | ----> Dipoles |  | 200 | nF |  | 200 | nF
9d
D1 & D2 | ----> Masse |  | 160 | nF |  | 160 | nF
Magnet | ----> Masse |  | * | 320 | nF | NAME: | Mehler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INDUCTANCE L/Q[10Hz] |  | Date of Test: | 2004-09-01 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
| [Value from gain phase analyser] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles |  | (L) | 21.7 | 21.9 |  | 21.8 | 21.9
|  | (Q) | 0.875 | 0.88 |  | 0.889 | 0.894
|  |  | N-3885P | N-3886P |  | N-3887P | N-3888P
D1 & D2 |  | (L) | 43.2 | mH |  | 43.4 | mH
|  | (Q) | 0.876 |  |  | 0.88
Magnet |  |  | (L) | 86.5 | mH
|  |  | (Q) | 0.881 |  | NAME: | Mehler
| INDUCTANCE L/Q[100Hz] |  | Date of Test: | 2004-09-01 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 20.9 | 20.8 |  | 20.9 | 20.9
|  | (Q) | 3.78 | 3.76 |  | 3.77 | 3.75
|  |  | N-3885P | N-3886P |  | N-3887P | N-3888P
D1 & D2 | * | (L) | 41.6 | mH |  | 41.7 | mH
|  | (Q) | 3.77 |  |  | 3.79
Magnet | * |  | (L) | 83.3 | mH
|  |  | (Q) | 3.78 |  | NAME: | Mehler
| INDUCTANCE L/Q[1.0KHz] |  | Date of Test: | 2004-09-01 | Equipment: | Kepco Power Supply [BM 297], Solartron Gain Phase Analyser [BM 298]
|  |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | [mH] | [mH] |  | [mH] | [mH] | 9c
Poles | * | (L) | 10.7 | 10.7 |  | 10.6 | 10.7
|  | (Q) | 1.12 | 1.16 |  | 1.12 | 1.16
|  |  | N-3885P | N-3886P |  | N-3887P | N-3888P
D1 & D2 | * | (L) | 21.3 | mH |  | 21.3 | mH
|  | (Q) | 1.15 |  |  | 1.14
Magnet | * |  | (L) | 43.2 | mH
|  |  | (Q) | 1.15 |  | NAME: | Mehler
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| INSULATION RESISTANCE |  | Date of Test: | 2004-09-01 | Equipment: | Megger BM21 [BM 00138]
[V = 1.0KV; 30'']
| Dipole D1 + QHs D1 | ----> Ground * |  | 5.3 | GW |  | >1000MW
[V = 1.0KV; 30'']
| Dipole D2 + QHs D2 | ----> Ground * |  | 5.3 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D1 (8x) | ----> D1 * |  | 1.51 | GW |  | >1000MW
[V = 1.0KV; 30'']
| QHs D2 (8x) | ----> D2 * |  | 1.56 | GW |  | >1000MW
DIPOLE 1 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 8.35 | GW |  | >1000MW
DIPOLE 2 | [5 empty] | [V = 1.0KV; 30'']
| Pole UP | ----> Pole LW * |  | 8.7 | GW |  | >1000MW
[5 empty] | NAME: | Mehler
| DIELECTRIC TESTS |  | Date of Test: | 2004-09-01 | Equipment: | Breakdown Tester BT1201 [BM 293 ]
[6 empty] | [V = 6.0KV; 5'] | ITP step 9f
| Dipole D1 + QHs D1 | ----> Ground * |  | 0.9 | µA |  | <15µA
[V = 6.0KV; 5']
| Dipole D2 + QHs D2 | ----> Ground * |  | 0.9 | µA |  | <15µA
[6 empty] | [V = 3.0KV; 5'] | ITP step 9h
| QHs D1 (8x) | ----> D1 * |  | 1.2 | µA |  | <10µA
[V = 3.0KV; 5']
| QHs D2 (8x) | ----> D2 * |  | 1.2 | µA |  | <10µA
DIPOLE 1 | [5 empty] | [V = 3.0KV; 5'] | ITP step 9g
| Pole UP | ----> Pole LW * |  | 0.8 | µA |  | <10µA
DIPOLE 2 | [5 empty] | [V = 3.0KV; 5']
| Pole UP | ----> Pole LW * |  | 0.7 | µA |  | <10µA
[5 empty] | NAME: | Mehler
| DISCHARGE TEST |  | Date of Test: | 2004-09-01 | Equipment: | Seitz Impulse Tester [BM 296]
| [V = 100V/turn; C = 2µF] |  | Apt 1 | [ext] |  | Apt 2 | [int] | ITP
|  |  | Upper | Lower |  | Upper | Lower | step
|  |  | msec | msec |  | msec | msec | 9i
| Poles [4.0KV] | * | 0.94 | 0.938 |  | 0.938 | 0.938
| Dipoles D1 & D2 [4KV] | * | 1.7 | msec |  | 1.7 | * | 9l
| Magnet [4KV] |  |  | 2.54 | *msec | NAME: | Mahler
| Quench Heaters |  | YT111 & 112 | YT121 & 122 |  | YT211 & 212 | YT221 & 222
| [V=1.6KV; C= 2µF] |  |  |  | µsec |  |  | µsec
NAME: |  | Current |  |  | A |  |  | A
ELECTRICAL TESTS OF DIPOLES
AFTER COLLARING
(WITH BEAM TUBES)
| DIQH TEST |  | Date of Test: | 2004-09-01 | Equipment: | DIGH equipment, Megger BM21 [BM138]
R[dc] Resistance
|  | YT111 / 112 | YT121 / 122 |  | YT211 / 212 | YT221 / 222
| R[dc] 4w | 22 | 22 | [W] | 21.9 | 22 | [W]
| R[dc] 4w | 21.7 | 21.4 | [W] | 21.7 | 21.5 | [W]
[6 empty] | NAME: | Mahler
Insulation Resistance
[5 empty] | [V = 3.0KV; 1'] |  | >1000MW
| QHs -> Ground | 4.4 |  | [GW] | 4.44 |  | [GW]
| QH -> Pol | 2.2 |  | [GW] | 2.44 |  | [GW]
[V = 3.0KV; 30'']
| Strip -> Strip | 7.6 | 7.3 | [GW] | 7.85 | 7.45 | [GW]
[6 empty] | NAME: | Mahler
| Discharge 850V 2.5kJ | Note: Before using 850V the QH's have to be measured with 450V! / Bemerkung: erst mit 450V messen, danach mit 850V!
|  | I [A] | t [ms] |  |  | I [A] | t [ms]
| YT111 | 38.3 | 149 |  | YT211 | 38.6 | 148
| YT112 | 38.1 | 147 |  | YT212 | 38.6 | 147
| YT121 | 38.2 | 149 |  | YT221 | 37.7 | 150
| YT122 | 39 | 145 |  | YT222 | 39.1 | 145
[6 empty] | NAME: | Mahler
Insulation Resistance
[5 empty] | [V = 3.0KV; 1'] |  | >1000MW
| QHs -> Ground | 4.24 |  | [GW] | 4.5 |  | [GW]
| QH -> Pol | 1.77 |  | [GW] | 1.81 |  | [GW]
[V = 3.0KV; 30'']
| Strip -> Strip | 7 | 7.15 | [GW] | 7.65 | 7.25 | [GW]
[6 empty] | NAME: | Mahler
R[dc] Resistance
|  | YT111 / 112 | YT121 / 122 |  | YT211 / 212 | YT221 / 222
| R[dc] 4w | 22 | 22 | [W] | 21.9 | 22.1 | [W]
| R[dc] 4w | 21.7 | 21.4 | [W] | 21.7 | 21.5 | [W]
[6 empty] | NAME: | Mahler
|  | 0 |  |  | 0
|  | 0 |  |  | 0
|  | 0 | 0 |  | 0 | 0
|  | 0 | 0 |  | 0 | 0
|  | 0 | 0 |  |  | 0
0
|  | test by |  | supervisor |  | approval
name |  | Mahler |  | Zehner |  | Zehner
company |  | BNM |  | BNN |  | BNN
date |  | 2004-09-01 |  | 2004-09-03 |  | 2004-09-03
signature
Note on C241: Formel für zu stark voneinander abweichende Isolationswerte an D1(QH -> Masse)
Note on C242: Formel für zu stark voneinander abweichende Isolationswerte an D1 (QH -> Pol)
Note on C243: Formel für zu stark voneinander abweichende Isolationswerte an D1 (Strip -> Strip)
Note on C244: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on C245: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on D16: 0 für die erste Messung, A für die 1. Wiederholung, B für die 2. Wiederholung, etc.
Note on D243: Formel für zu stark voneinander abweichende Isolationswerte an D1 (Strip -> Strip)
Note on D244: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on D245: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on F241: Formel für zu stark voneinander abweichende Isolationswerte an D1(QH -> Masse)
Note on F242: Formel für zu stark voneinander abweichende Isolationswerte an D1 (QH -> Pol)
Note on F243: Formel für zu stark voneinander abweichende Isolationswerte an D1 (Strip -> Strip)
Note on F244: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on F245: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on G243: Formel für zu stark voneinander abweichende Isolationswerte an D1 (Strip -> Strip)
Note on G244: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on G245: Formel für zu stark voneinander abweichende Widerstandswerte an D1
Note on H16: Y, wenn die Messung nach einer Reparatur durchgeführt wurde, N, wenn vor dieser Messung keine Reparatur durchgeführt wurde
Apt1
Apt2
Up
Lw
Dip
Magnet
REQUIREMENTS OF TEST OBJECT/SPECIFICATION:
CERN:
BNN:
LHC-MMS/98-198 Rev. 2.0 Annex B10 TABLE C
Arbeitsanweisung CA0014_0