## Alarm sheet
File name | HCMB__A001-03000015_cc.xls
Component ID | HCMB__A001 |  |  |  | Serial Number | 3000015
Date of test Ap 1 | 2002-11-25 |  |  |  | Date of test Ap 2 | 2002-11-26
| Aperture 1 |  |  |  |  | Aperture 2
Magnetic length | status ok |  |  |  | Magnetic length | status ok
| Average straight | Variation straight | Heads CS | Heads NCS |  | Average straight | Variation straight | Heads CS | Heads NCS
| positions 2 to 19 | positions 2 to 19 | position 1 | position 20 |  | positions 2 to 19 | positions 2 to 19 | position 1 | position 20
Main field | status ok | status ok | status ok | status ok | Main field | status ok | status ok | status ok | status ok
Angle |  | status ok | status ok | status ok | Angle |  | status ok | status ok | status ok
b2 | status ok | status ok | status ok | status ok | b2 | status ok | status ok | status ok | status ok
b3 | status ok | status ok | status ok | status ok | b3 | status ok | status ok | status ok | status ok
b4 | status ok | status ok | status ok | status ok | b4 | status ok | status ok | status ok | status ok
b5 | status ok | status ok | status ok | status ok | b5 | status ok | status ok | status ok | status ok
b6 | status ok | status ok | status ok | status ok | b6 | status ok | yellow alarm | status ok | status ok
b7 | status ok | status ok | status ok | status ok | b7 | status ok | status ok | status ok | status ok
b8 | status ok | status ok | status ok | status ok | b8 | status ok | status ok | status ok | status ok
b9 | status ok | status ok | status ok | status ok | b9 | status ok | status ok | status ok | status ok
b10 | status ok | status ok | status ok | status ok | b10 | status ok | yellow alarm | status ok | status ok
b11 | status ok | status ok | status ok | status ok | b11 | status ok | status ok | status ok | status ok
b12 | status ok | status ok | status ok | status ok | b12 | status ok | status ok | status ok | status ok
b13 | status ok | status ok | status ok | status ok | b13 | status ok | status ok | status ok | status ok
b14 | status ok | status ok | status ok | status ok | b14 | status ok | status ok | status ok | status ok
b15 | status ok | status ok | status ok | status ok | b15 | status ok | status ok | status ok | status ok
a2 | status ok | status ok | status ok | status ok | a2 | status ok | status ok | status ok | status ok
a3 | status ok | status ok | status ok | status ok | a3 | status ok | status ok | status ok | status ok
a4 | status ok | status ok | status ok | status ok | a4 | status ok | status ok | status ok | status ok
a5 | status ok | status ok | status ok | status ok | a5 | status ok | status ok | status ok | status ok
a6 | status ok | status ok | status ok | status ok | a6 | status ok | status ok | status ok | status ok
a7 | status ok | status ok | status ok | status ok | a7 | status ok | status ok | status ok | status ok
a8 | status ok | status ok | status ok | status ok | a8 | status ok | status ok | status ok | status ok
a9 | status ok | status ok | status ok | yellow alarm | a9 | status ok | status ok | status ok | yellow alarm
a10 | status ok | status ok | status ok | status ok | a10 | status ok | status ok | status ok | status ok
a11 | status ok | status ok | status ok | status ok | a11 | status ok | status ok | status ok | status ok
a12 | status ok | status ok | status ok | status ok | a12 | status ok | status ok | status ok | status ok
a13 | status ok | status ok | status ok | status ok | a13 | status ok | status ok | status ok | status ok
a14 | status ok | status ok | status ok | status ok | a14 | status ok | status ok | status ok | status ok
a15 | status ok | status ok | status ok | status ok | a15 | status ok | status ok | status ok | status ok
Coil Positioning | status ok |  |  |  | Coil Positioning | status ok
Field Colinearity | status ok

## Original data
File name |  | HCMB__A001-03000015_cc.xls | [19 empty] | File name | 0 | HCMB__A001-03000015_cc.xls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Component ID |  | HCMB__A001 |  |  | Serial Number |  |  | 3000015 | [11 empty] | Signs |  | Component ID | 0 | HCMB__A001 | 0 | 0 | Serial Number | 0 | 0 | 3000015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Signs | 0 | 0
Ref. Test Proced. |  | CERN IT 2708/LHC/LHC Rev 2.0 Annex b.18 | [16 empty] | b even | 1 |  | Ref. Test Proced. | 0 | CERN IT 2708/LHC/LHC Rev 2.0 Annex b.18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | b even | 1 | 0 | 0
Firm Name |  | Noell | [9 empty] | File name for aperture 1 |  |  | noell15cct1_1 |  |  |  | a odd | 1 |  | Firm Name | 0 | Noell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | File name for aperture 1 | 0 | 0 | noell15cct1_1 | 0 | 0 | 0 | a odd | 1 | 0 | 0
Test Type |  | Magnetic Measures |  |  | ITP number |  |  | 21 |  |  |  | File name for aperture 2 |  |  | noell15cct2_1 |  |  |  | a even | 1 |  | Test Type | 0 | Magnetic Measures | 0 | 0 | ITP number | 0 | 0 | 21 | 0 | 0 | 0 | File name for aperture 2 | 0 | 0 | noell15cct2_1 | 0 | 0 | 0 | a even | 1 | 0 | 0
Test Operator |  | Zehner/Moresi |  |  | Test Controller |  |  | E. Todesco | [13 empty] | Test Operator | 0 | Zehner/Moresi | 0 | 0 | Test Controller | 0 | 0 | E. Todesco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Aperture 1 | [11 empty] | Aperture 2 | [9 empty] | Aperture 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Aperture 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Date of test |  | 2002-11-25 |  |  | Time of test |  |  | 13:00 - 16:00 |  |  |  | Date of test |  | 2002-11-26 |  |  | Time of test |  |  | 9:30 - 13:00 |  | Date of test | 0 | 2002-11-25 | 0 | 0 | Time of test | 0 | 0 | 13:00 - 16:00 | 0 | 0 | 0 | Date of test | 0 | 2002-11-26 | 0 | 0 | Time of test | 0 | 0 | 9:30 - 13:00 | 0 | 0
Mole name |  | Dipole 11 |  |  | Calibration date |  |  | 2002-04-17 |  |  |  | Mole name |  | Dipole 11 |  |  | Calibration date |  |  | 2002-04-17 |  | Mole name | 0 | Dipole 11 | 0 | 0 | Calibration date | 0 | 0 | 2002-04-17 | 0 | 0 | 0 | Mole name | 0 | Dipole 11 | 0 | 0 | Calibration date | 0 | 0 | 2002-04-17 | 0 | 0
Coil length (m) |  | 0.7499 |  |  | Coil temperature |  |  | 22 |  |  |  | Coil length (m) |  | 0.7499 |  |  | Coil temperature |  |  | 22 |  | Coil length (m) | 0 | 0.7499 | 0 | 0 | Coil temperature | 0 | 0 | 22 | 0 | 0 | 0 | Coil length (m) | 0 | 0.7499 | 0 | 0 | Coil temperature | 0 | 0 | 22 | 0 | 0
Excitation current (A) |  | 8.5 |  |  | Analysis tools |  |  | dri,rot,nor,cel,fdw |  |  |  | Excitation current (A) |  | 8.5 |  |  | Analysis tools |  |  | dri,rot,nor,cel,fdw |  | Excitation current (A) | 0 | 8.5 | 0 | 0 | Analysis tools | 0 | 0 | dri,rot,nor,cel,fdw | 0 | 0 | 0 | Excitation current (A) | 0 | 8.5 | 0 | 0 | Analysis tools | 0 | 0 | dri,rot,nor,cel,fdw | 0 | 0
N. points |  | 20 |  |  | N. measure |  |  | 10 (5+,5-) |  |  |  | N. points |  | 20 |  |  | N. measure |  |  | 10 (5+,5-) |  | N. points | 0 | 20 | 0 | 0 | N. measure | 0 | 0 | 10 (5+,5-) | 0 | 0 | 0 | N. points | 0 | 20 | 0 | 0 | N. measure | 0 | 0 | 10 (5+,5-) | 0 | 0
Rotation speed |  | 0.6 |  |  | I. Gain |  |  | 50/500 |  |  |  | Rotation speed |  | 0.6 |  |  | I. Gain |  |  | 50/500 |  | Rotation speed | 0 | 0.6 | 0 | 0 | I. Gain | 0 | 0 | 50/500 | 0 | 0 | 0 | Rotation speed | 0 | 0.6 | 0 | 0 | I. Gain | 0 | 0 | 50/500 | 0 | 0
Dx average |  | 0.00023944 |  |  | Dy average |  |  | 0.00030863 |  |  |  | Dx average |  | 0.00026835 |  |  | Dy average |  |  | 0.0003563 |  | Dx average | 0 | 0.00023944 | 0 | 0 | Dy average | 0 | 0 | 0.00030863 | 0 | 0 | 0 | Dx average | 0 | 0.00026835 | 0 | 0 | Dy average | 0 | 0 | 0.0003563 | 0 | 0
Magnetic length |  | 14.457 |  |  | Tranfs. Function (mT/KA) |  |  | 596.2222 |  |  |  | Magnetic length |  | 14.4604 |  |  | Tranfs. Function (mT/KA) |  |  | 596.268 |  | Magnetic length | 0 | 14.457 | 0 | 0 | Tranfs. Function (mT/KA) | 0 | 0 | 596.2222 | 0 | 0 | 0 | Magnetic length | 0 | 14.4604 | 0 | 0 | Tranfs. Function (mT/KA) | 0 | 0 | 596.268 | 0 | 0
Phase |  | 3.9413 |  |  | Integral field (T.m) |  |  | 0.073267 |  |  |  | Phase |  | 3.9288 |  |  | Integral field (T.m) |  |  | 0.07329 |  | Phase | 0 | 3.9413 | 0 | 0 | Integral field (T.m) | 0 | 0 | 0.073267 | 0 | 0 | 0 | Phase | 0 | 3.9288 | 0 | 0 | Integral field (T.m) | 0 | 0 | 0.07329 | 0 | 0
File | Aperture 1 - Collared coils | [19 empty] | Integrals | File | Aperture 2 - Collared coils | [19 empty] | Integrals
C1 (T) | 0.003228 | 0.005071 | 0.005067 | 0.005068 | 0.005067 | 0.005067 | 0.005068 | 0.005068 | 0.005068 | 0.005067 | 0.005067 | 0.005068 | 0.005067 | 0.005068 | 0.005067 | 0.005068 | 0.005067 | 0.005068 | 0.005071 | 0.003252 | 0.073267 | C1 (T) | 0.003256 | 0.00507 | 0.005068 | 0.005068 | 0.005067 | 0.005068 | 0.005068 | 0.005067 | 0.005068 | 0.005068 | 0.005069 | 0.005068 | 0.005068 | 0.005068 | 0.005068 | 0.005068 | 0.005068 | 0.005068 | 0.005072 | 0.003247 | 0.07329
Angle (mrad) | 5.0455 | -0.28366 | -0.99624 | -1.4006 | -1.1345 | -0.86363 | -0.28741 | 0.8436 | 0.98871 | 0.68847 | 0.29679 | 0.50213 | 0.39834 | 0.45756 | 0.29501 | -0.25994 | -0.59808 | -0.43064 | -0.88079 | -0.93303 | 3.9413 | Angle (mrad) | 4.6056 | -0.11916 | -1.0264 | -1.2498 | -0.76816 | -0.66277 | -0.18648 | 0.59425 | 0.91275 | 0.42992 | 0.37603 | 0.50802 | 0.52609 | 0.6003 | -0.086677 | -0.32122 | -0.76546 | -0.46679 | -0.49312 | -1.1204 | 3.9288
Multipoles | Position 1 | Position 2 | Position 3 | Position 4 | Position 5 | Position 6 | Position 7 | Position 8 | Position 9 | Position 10 | Position 11 | Position 12 | Position 13 | Position 14 | Position 15 | Position 16 | Position 17 | Position 18 | Position 19 | Position 20 |  | Multipoles | Position 1 | Position 2 | Position 3 | Position 4 | Position 5 | Position 6 | Position 7 | Position 8 | Position 9 | Position 10 | Position 11 | Position 12 | Position 13 | Position 14 | Position 15 | Position 16 | Position 17 | Position 18 | Position 19 | Position 20
b1 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | b1 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000
b2 | -1.1065 | -1.8643 | -1.7945 | -2.0648 | -1.6547 | -1.2586 | -1.9746 | -2.0602 | -2.0482 | -0.72977 | -2.1074 | -1.5987 | -1.2147 | -1.1209 | -1.4765 | -1.2707 | -0.10583 | -1.4567 | -2.1294 | -2.2993 | -1.5619 | b2 | 3.6742 | 1.3618 | 1.648 | 1.6861 | 1.9797 | 2.9188 | 2.3245 | 2.9294 | 2.5089 | 1.6461 | 1.2312 | 1.9397 | 2.0319 | 1.6446 | 0.66546 | 1.6635 | 1.1066 | 1.2006 | 1.8597 | 1.2941 | 1.8428
b3 | 36.9244 | -0.51148 | -0.16674 | 0.17874 | -0.13966 | -0.35273 | 1.0182 | 0.054169 | 0.057326 | 0.21665 | -0.010198 | -0.5176 | -0.076344 | -0.89824 | -0.14094 | -0.01924 | 0.41097 | -0.49749 | -0.36958 | -0.72082 | 1.1044 | b3 | 35.848 | -0.96252 | -0.81068 | -0.47497 | -0.32193 | -1.7279 | 0.46052 | -0.40835 | -0.35097 | -0.78394 | -1.138 | -1.3588 | -0.45723 | -1.1551 | -0.55109 | 0.58845 | 0.78626 | -0.85738 | -0.022038 | -0.76617 | 0.67376
b4 | -0.071183 | 0.051785 | 0.12911 | -0.12728 | -0.10815 | -0.13811 | -0.13824 | -0.15086 | 0.010011 | 0.088925 | -0.060551 | 0.16825 | 0.053965 | -0.18394 | -0.24464 | -0.08641 | -0.00091216 | 0.13888 | -0.15254 | -0.50037 | -0.057948 | b4 | 0.10494 | -0.10124 | 0.22671 | 0.27296 | 0.49378 | 0.17791 | 0.3348 | 0.085569 | 0.064158 | 0.48212 | 0.38035 | 0.20093 | 0.36511 | 0.084708 | -0.032569 | 0.081259 | -0.15731 | -0.26304 | 0.19207 | -0.14382 | 0.1485
b5 | -3.6812 | 0.019171 | -0.30337 | 0.14568 | 0.13917 | 0.35254 | 0.228 | 0.34477 | 0.20091 | 0.34547 | 0.68705 | 0.22858 | 0.27386 | 0.54483 | 0.25188 | 0.23531 | 0.040419 | 0.24215 | 0.1418 | -3.4566 | -0.023051 | b5 | -4.4252 | -0.44308 | -0.27541 | -0.24357 | -0.28755 | 0.040316 | -0.10963 | 0.22786 | 0.034885 | -0.38266 | 0.15541 | 0.0093049 | -0.17104 | 0.18079 | -0.058396 | 0.089298 | -0.0016341 | 0.038882 | -0.11821 | -3.6159 | -0.33574
b6 | 0.16583 | 0.1376 | 0.090193 | 0.080947 | -0.015888 | -0.08443 | 0.08685 | 0.11888 | 0.029652 | -0.12615 | 0.080442 | 0.1279 | 0.0077351 | -0.14314 | -0.041878 | -0.0024439 | -0.026296 | 0.041599 | 0.044464 | -0.020754 | 0.025856 | b6 | 0.36798 | 0.12293 | 0.076544 | 0.04192 | -0.047099 | -0.3296 | -0.056453 | -0.15208 | -0.12872 | -0.0025041 | 0.12646 | -0.14529 | 0.068379 | 0.00056698 | 0.030631 | 0.011938 | -0.032782 | 0.034583 | 0.15182 | -0.045865 | -0.0011148
b7 | 2.9665 | 0.95309 | 1.0884 | 1.1695 | 1.1205 | 1.115 | 1.067 | 1.1308 | 1.1617 | 1.0902 | 1.0695 | 1.1183 | 1.1568 | 1.1002 | 1.1448 | 1.2039 | 1.1783 | 1.2409 | 1.1748 | 0.77977 | 1.1761 | b7 | 2.8678 | 0.93392 | 0.98059 | 1.0645 | 1.0914 | 0.9665 | 1.0373 | 1.1872 | 1.1607 | 1.0631 | 1.0464 | 1.0621 | 1.1016 | 1.1046 | 1.0495 | 1.1397 | 1.1251 | 1.1261 | 1.0442 | 0.76894 | 1.1212
b8 | -0.030943 | 0.08221 | 0.0044636 | 0.035683 | 0.010738 | -0.00049327 | -0.0022855 | -0.040196 | 0.0040277 | -0.0037244 | 0.0022393 | 0.0065824 | 0.0036627 | 0.048358 | 0.0093122 | 0.020134 | -0.037869 | -0.039497 | -0.023856 | 0.019434 | 0.0037483 | b8 | 0.070148 | 0.074678 | 0.045808 | -0.0012362 | -0.074507 | -0.035044 | -0.050681 | -0.077474 | -0.063725 | -0.068154 | -0.0086611 | -0.024193 | -0.00051476 | -0.050522 | -0.029019 | 0.0081077 | -0.0058195 | -0.052662 | 0.012183 | -0.0030947 | -0.01858
b9 | 0.41748 | 0.48033 | 0.47543 | 0.49639 | 0.48646 | 0.47147 | 0.48176 | 0.46554 | 0.46736 | 0.48209 | 0.46702 | 0.47194 | 0.48727 | 0.48244 | 0.49074 | 0.49499 | 0.50595 | 0.50598 | 0.48864 | 0.45493 | 0.48031 | b9 | 0.40953 | 0.50185 | 0.46583 | 0.46086 | 0.47877 | 0.49299 | 0.49794 | 0.49976 | 0.49546 | 0.47507 | 0.48378 | 0.47866 | 0.48822 | 0.47122 | 0.44244 | 0.45232 | 0.47597 | 0.48097 | 0.47231 | 0.42978 | 0.47466
b10 | 0.023821 | 0.079762 | -0.0027221 | 0.091372 | 0.04863 | 0.0054363 | 0.075746 | 0.034913 | 0.019205 | -0.029158 | 0.049485 | 0.0085797 | -0.029362 | -0.1005 | -0.015398 | -0.023901 | -0.091713 | -0.077417 | -0.038352 | -0.030889 | 0 | b10 | 0.15019 | 0.18374 | -0.017043 | 0.021284 | -0.029485 | -0.052822 | -0.019017 | -0.10242 | -0.045952 | -0.047526 | 0.10773 | 0.02662 | 0.027456 | -0.067634 | -0.016313 | -0.0037556 | -0.015409 | -0.03852 | 0.019275 | -0.041861 | 0
b11 | 0.65413 | 0.76241 | 0.75184 | 0.76288 | 0.76506 | 0.77742 | 0.77114 | 0.77666 | 0.76717 | 0.76579 | 0.77845 | 0.76865 | 0.77112 | 0.77935 | 0.76979 | 0.7656 | 0.7631 | 0.76944 | 0.76212 | 0.68334 | 0.76163 | b11 | 0.65105 | 0.76654 | 0.76278 | 0.76737 | 0.75856 | 0.77901 | 0.76646 | 0.76226 | 0.75913 | 0.76814 | 0.78574 | 0.77834 | 0.76729 | 0.76654 | 0.76765 | 0.75872 | 0.75977 | 0.7652 | 0.76987 | 0.6852 | 0.76059
b12 | -0.0078914 | 0.0032538 | -0.0066675 | 0.0071259 | 0.0053677 | -0.0020543 | 0.0032101 | -0.0046778 | 0.00016275 | -0.0032812 | 0.00069595 | -0.0034372 | -0.00099686 | -0.0026816 | 0.0041627 | -0.0032112 | -0.011544 | -0.013591 | -0.004012 | 0.00076481 | -0.001904 | b12 | 0.028899 | 0.023122 | 0.00078119 | 0.0012049 | 0.0014174 | 0.0092032 | 0.0055472 | -0.002776 | 0.00123 | 0.0034077 | 0.015501 | 0.0099268 | 0.0097503 | -0.0078054 | 0.00021061 | 0.00084608 | 0.0036288 | -0.0012842 | 0.0037075 | -0.0074219 | 0.004742
b13 | 0.088954 | 0.070811 | 0.075979 | 0.070949 | 0.068208 | 0.069577 | 0.069658 | 0.070105 | 0.070429 | 0.068681 | 0.064828 | 0.071512 | 0.071989 | 0.066743 | 0.069738 | 0.072042 | 0.072658 | 0.071323 | 0.072591 | 0.053167 | 0.070472 | b13 | 0.088535 | 0.07378 | 0.071784 | 0.069506 | 0.070308 | 0.061328 | 0.064644 | 0.065548 | 0.065266 | 0.069041 | 0.061628 | 0.06485 | 0.068613 | 0.065543 | 0.067437 | 0.070196 | 0.069565 | 0.069266 | 0.07085 | 0.052866 | 0.06793
b14 | 0.0032961 | -0.0029784 | -0.0068003 | -0.002143 | -0.0036416 | -0.0057197 | -0.0039016 | -0.0050413 | -0.0047105 | -0.0072273 | -0.0046932 | -0.0079761 | -0.0070089 | -0.010884 | -0.0064117 | -0.0076817 | -0.0085923 | -0.0086893 | -0.0075185 | -0.0032447 | -0.0057886 | b14 | 0.0015905 | 0.0041546 | -0.009027 | -0.0076941 | -0.0075516 | -0.0080452 | -0.0072209 | -0.010326 | -0.0086822 | -0.0066076 | -0.00035296 | -0.0046911 | -0.0037288 | -0.0093413 | -0.0076468 | -0.006718 | -0.0059998 | -0.0067553 | -0.0052339 | -0.0050206 | -0.0058942
b15 | -0.0080025 | 0.031109 | 0.024468 | 0.026128 | 0.026214 | 0.02528 | 0.027842 | 0.02783 | 0.027706 | 0.024335 | 0.029308 | 0.027432 | 0.026013 | 0.025787 | 0.027475 | 0.023806 | 0.01874 | 0.022943 | 0.024944 | 0.0061476 | 0.024183 | b15 | -0.010775 | 0.028991 | 0.026886 | 0.027223 | 0.022958 | 0.024678 | 0.024136 | 0.022345 | 0.024472 | 0.022749 | 0.028569 | 0.027043 | 0.027809 | 0.025083 | 0.026714 | 0.025966 | 0.023126 | 0.022071 | 0.025031 | 0.0031618 | 0.023386
b16 | [21 empty] | b16
b17 | [21 empty] | b17
a1 | 50.4555 | -2.8366 | -9.9624 | -14.0055 | -11.3446 | -8.6363 | -2.8741 | 8.436 | 9.8871 | 6.8847 | 2.9679 | 5.0213 | 3.9834 | 4.5756 | 2.9501 | -2.5994 | -5.9808 | -4.3064 | -8.8079 | -9.3303 | 0 | a1 | 46.0564 | -1.1916 | -10.2643 | -12.4982 | -7.6815 | -6.6277 | -1.8648 | 5.9425 | 9.1275 | 4.2992 | 3.7603 | 5.0802 | 5.2609 | 6.003 | -0.86677 | -3.2122 | -7.6546 | -4.6679 | -4.9312 | -11.2041 | 0
a2 | -2.2543 | -0.5225 | -0.40533 | -0.20809 | 0.84523 | -0.47805 | -0.75909 | -0.78825 | 0.038656 | -0.14885 | 1.0404 | 0.44199 | -0.90635 | -0.15107 | -0.7941 | -0.23114 | -0.58939 | -0.016584 | -0.22082 | -0.091552 | -0.27742 | a2 | -0.050569 | -2.0627 | -2.3266 | -3.5006 | -2.7698 | -0.79251 | -1.822 | -2.9709 | -3.1933 | -0.94332 | -0.94807 | -1.9975 | -2.2265 | -1.6409 | -1.0989 | -1.6136 | -1.8887 | -0.45239 | -0.67103 | 6.1749 | -1.5036
a3 | -1.5768 | 0.92985 | 0.58326 | 0.56756 | 0.37085 | 0.0060813 | 0.26901 | 0.50621 | 0.94619 | 0.62702 | 0.25382 | 0.7205 | 0.33254 | 0.16496 | 0.23149 | 0.069836 | 0.82219 | 1.0315 | 0.50846 | 0.13656 | 0.41627 | a3 | 0.65035 | 0.58533 | 0.48578 | 0.61176 | 0.78206 | 1.1065 | 0.91963 | 0.67583 | 0.47622 | 0.3553 | 0.33936 | 0.76036 | 0.6855 | 0.8232 | 0.053931 | -0.051754 | 0.035004 | 0.68925 | -0.243 | 0.58866 | 0.5126
a4 | 0.66837 | -0.27018 | -0.31872 | -0.14226 | -0.25155 | -0.58669 | -0.30961 | -0.083621 | -0.10392 | -0.38742 | -0.13162 | 0.019514 | -0.0031355 | -0.13523 | 0.56506 | 0.31048 | -0.11966 | 0.14284 | 0.017552 | -0.3592 | -0.082625 | a4 | 0.21335 | 0.21805 | -0.15458 | -0.065272 | 0.036673 | -0.48743 | 0.24741 | 0.1301 | 0.10738 | 0.27603 | 0.28072 | -0.14308 | 0.018238 | -0.54329 | 0.26997 | 0.29912 | 0.40652 | -0.066867 | 0.23731 | 0.55461 | 0.080879
a5 | 2.4262 | 0.17163 | 0.10768 | 0.010103 | 0.021734 | 0.0041218 | 0.13352 | 0.1294 | 0.2473 | -0.038951 | 0.018569 | 0.14921 | 0.0064507 | 0.098284 | -0.087886 | -0.035881 | -0.01623 | 0.12026 | -0.07067 | -0.24564 | 0.12222 | a5 | 3.2786 | 0.080686 | -0.0010536 | 0.010542 | -0.25821 | -0.036086 | -0.09996 | -0.1037 | -0.12133 | -0.21156 | -0.1741 | -0.077797 | -0.27683 | -0.090354 | -0.1402 | -0.13556 | -0.092718 | -0.11669 | -0.14913 | 0.092605 | 0.008901
a6 | -0.011446 | -0.14094 | 0.0090321 | 0.10249 | 0.090952 | -0.021179 | -0.088369 | 0.016769 | 0.074988 | 0.15859 | 0.2923 | 0.14407 | 0.13761 | 0.16329 | 0.12787 | 0.1306 | 0.095813 | 0.11313 | 0.039413 | -0.083354 | 0.071867 | a6 | 0.27602 | 0.051468 | 0.10945 | -0.010856 | 0.1861 | 0.36578 | 0.24699 | 0.26729 | 0.29582 | 0.25318 | 0.39535 | 0.29583 | 0.18769 | 0.089836 | 0.056289 | 0.030133 | -0.038091 | 0.12212 | 0.14687 | 0.31205 | 0.1778
a7 | 1.4746 | -0.071754 | -0.070866 | -0.074172 | -0.05805 | -0.0065121 | -0.074437 | -0.05896 | -0.03751 | -0.010458 | 0.03708 | 0.023431 | -0.049783 | -0.058515 | -0.092783 | -0.054597 | -0.090285 | -0.013444 | -0.0556 | 0.039553 | 0.0076647 | a7 | 1.7391 | -0.057963 | -0.05468 | -0.08427 | -0.14095 | -0.12407 | -0.085089 | -0.049335 | -0.066197 | -0.12943 | -0.0708 | -0.091141 | -0.035322 | 0.046709 | -0.071858 | -0.099677 | -0.11289 | 0.045054 | -0.034697 | 0.044182 | -0.0037035
a8 | 0.009668 | 0.012118 | 0.080493 | 0.084749 | 0.047205 | 0.04972 | 0.068499 | 0.068447 | 0.055011 | 0.075783 | 0.075837 | 0.080649 | 0.048454 | 0.058756 | 0.027073 | 0.077271 | 0.093345 | 0.069918 | 0.031025 | 0.0031091 | 0.057705 | a8 | -0.027275 | 0.043649 | 0.0044839 | -0.0099936 | -0.0025449 | -0.090524 | 0.025037 | 0.019019 | 0.036054 | -0.046538 | -0.010401 | -0.014289 | -0.026167 | -0.024859 | -0.048134 | -0.037773 | -0.013686 | -0.0065048 | -0.03867 | 0.0084436 | -0.013169
a9 | -0.30846 | -0.047977 | -0.040823 | -0.033042 | -0.045504 | 0.0051514 | 0.0072831 | -0.039137 | -0.03926 | -0.017796 | -0.026643 | -0.022201 | -0.039865 | -0.024966 | -0.018145 | -0.024263 | -0.041144 | -0.025798 | -0.054533 | -0.090711 | -0.040622 | a9 | -0.1788 | 0.001407 | -0.01211 | -0.040234 | -0.057542 | -0.058653 | -0.015163 | 0.0060433 | -0.017623 | -0.021861 | -0.018258 | -0.0079532 | -0.012596 | -0.049435 | -0.066311 | -0.037132 | -0.046486 | -0.05334 | -0.024515 | -0.084264 | -0.036341
a10 | -0.048571 | -0.030957 | 0.022433 | 0.022704 | 0.0055727 | 0.032297 | 0.015037 | -0.028274 | -0.035715 | 0.0053697 | -0.0011175 | 0.023455 | 0.0060669 | -0.02142 | -0.039653 | 0.00027294 | 0.053177 | 0.0035286 | -0.0055389 | 0.0058084 | 0 | a10 | 0.077972 | 0.019965 | 0.018356 | -0.052821 | 0.021206 | -0.0061805 | 0.016292 | 0.0054906 | -0.0081716 | -0.013995 | 0.0014852 | 0.012167 | -0.038452 | -0.050108 | -0.043384 | -0.046364 | 0.0063387 | 0.040905 | 0.047863 | 0.030073 | 0
a11 | 0.14866 | -0.078374 | -0.081958 | -0.078284 | -0.070032 | -0.053641 | -0.061926 | -0.054623 | -0.053238 | -0.053695 | -0.050091 | -0.05939 | -0.0629 | -0.066391 | -0.069425 | -0.06916 | -0.075476 | -0.061989 | -0.070753 | -0.06177 | -0.057882 | a11 | 0.17767 | -0.075861 | -0.07978 | -0.073721 | -0.072479 | -0.080509 | -0.060355 | -0.053244 | -0.050447 | -0.060385 | -0.056137 | -0.064082 | -0.059014 | -0.05084 | -0.072353 | -0.067959 | -0.072619 | -0.058326 | -0.06401 | -0.061925 | -0.056942
a12 | -0.013036 | -0.010223 | -0.0018041 | -0.0042869 | -0.0033459 | -0.0074111 | -0.0072388 | -0.0083867 | -0.0078713 | -0.0059329 | 0.0065399 | 0.00093021 | -0.0019734 | -0.0049661 | -0.0093697 | -0.0051654 | 0.0025303 | -0.00096504 | -0.001047 | -0.0034265 | -0.0041753 | a12 | 0.0022276 | -0.0015296 | 0.002154 | -0.010785 | 0.0040001 | 0.010067 | 0.00088579 | 0.00076003 | 0.001642 | 0.0004408 | 0.0087888 | 0.0066019 | -0.00082903 | 0.004461 | -0.001665 | -0.0044703 | -0.0031448 | 0.0059709 | 0.0074523 | 0.0037063 | 0.0017948
a13 | -0.027618 | -0.0041321 | -0.0054115 | -0.0068115 | -0.0062593 | -0.0030203 | -0.0040482 | -0.0043036 | -0.0019716 | -0.0011869 | -0.0029345 | -0.0019382 | -0.0028604 | -3.9574e-05 | -0.0074154 | -0.0079031 | -0.0064563 | -0.0022933 | -0.0069987 | -0.0061182 | -0.0050552 | a13 | -0.016507 | -0.0068934 | -0.0060293 | -0.0081294 | -0.009749 | -0.0062491 | -0.0036494 | -0.0025686 | -0.004466 | -0.0066619 | -0.0056262 | -0.0056716 | -0.0069785 | -0.0025555 | -0.0074111 | -0.0094721 | -0.0092736 | -0.0085665 | -0.0073538 | -0.0065962 | -0.0068543
a14 | 0.0055147 | -0.0092073 | -0.0068393 | -0.0086593 | -0.0093791 | -0.0081214 | -0.0081685 | -0.0082302 | -0.0075749 | -0.0084622 | -0.0099922 | -0.0094641 | -0.0099143 | -0.0095295 | -0.010172 | -0.0064507 | -0.0036561 | -0.0050551 | -0.0068489 | -0.003601 | -0.0074968 | a14 | 0.0047681 | -0.0045201 | -0.0058854 | -0.0071797 | -0.0028866 | -0.0098619 | -0.0059232 | -0.0051436 | -0.0036837 | -0.004952 | -0.0071325 | -0.0058456 | -0.0074757 | -0.008593 | -0.0056153 | -0.0055336 | -0.0010731 | -0.0037307 | -0.0040847 | -0.00095995 | -0.0050131
a15 | 0.0010005 | -0.0042833 | -0.0073064 | -0.0036715 | -0.0044666 | -0.0047941 | -0.0027489 | -0.0062258 | -0.0063439 | -0.0071783 | -0.0060145 | -0.0064741 | -0.008923 | -0.010293 | -0.0084625 | -0.0085925 | -0.0071957 | -0.009118 | -0.0083598 | -0.0029358 | -0.0063117 | a15 | 0.008265 | -0.0012478 | -0.0092556 | -0.010183 | -0.010327 | -0.010902 | -0.0067978 | -0.010715 | -0.011777 | -0.0087919 | -0.0036212 | -0.0053323 | -0.0070275 | -0.013284 | -0.010438 | -0.010734 | -0.0093732 | -0.0059533 | -0.0058202 | -0.0040654 | -0.0077209
a16 | [21 empty] | a16
a17 | [21 empty] | a17
Dx (m) | -3.1633e-05 | -0.00018296 | 1.1543e-05 | -0.00019647 | -0.00010606 | 0 | -0.00016333 | -8.0338e-05 | -4.7799e-05 | 6.525e-05 | -0.00010777 | -1.4883e-05 | 6.5389e-05 | 0.00021363 | 2.59e-05 | 5.2698e-05 | 0.00021407 | 0.00017069 | 8.3687e-05 | 7.7514e-05 | 0.00023944 | Dx (m) | -0.0004184 | -0.00040025 | 4.1803e-05 | -5.7807e-05 | 6.997e-05 | 0.00011265 | 4.4745e-05 | 0.00022815 | 0.00010124 | 0.0001021 | -0.00023187 | -5.5576e-05 | -6.6986e-05 | 0.0001421 | 2.6836e-05 | 0 | 3.5507e-05 | 9.1941e-05 | -3.3514e-05 | 0.00010971 | 0.00026835
Dy (m) | 0.00013331 | 5.0341e-05 | -4.9472e-05 | -7.0725e-05 | -2.2083e-05 | -7.1122e-05 | -4.6187e-05 | 5.6226e-05 | 7.5813e-05 | 0 | 0 | -5.3021e-05 | 0 | 6.4982e-05 | 8.9872e-05 | 0 | -9.7444e-05 | 0 | 2.013e-05 | 0 | 0.00030863 | Dy (m) | -9.0327e-05 | -8.4192e-05 | -3.6536e-05 | 0.00011143 | -4.0839e-05 | 2.5053e-05 | -3.2605e-05 | 0 | 2.5013e-05 | 3.8978e-05 | -2.0019e-05 | -3.1167e-05 | 8.0082e-05 | 0.00012062 | 9.8602e-05 | 0.00010379 | -1.0786e-05 | -8.387e-05 | -0.00010846 | -6.4747e-05 | 0.0003563
Magnetic length (m) |  | 14.457 | [19 empty] | Magnetic length (m) |  | 14.4604
Transfer funct. (mT/KA) |  | 596.2222 | [19 empty] | Transfer funct. (mT/KA) |  | 596.268
Coil positioning (mm) |  | 0.020794 | [19 empty] | Coil positioning (mm) |  | 0.025907
Current (A) |  | 8.5 | [19 empty] | Current (A) |  | 8.5 | [7 empty] | Prüfer / Tester |  |  |  | Prüfausfsicht / Supervisor |  |  |  | Freigabe / Approval
|  |  |  | Auftrag-Nr.: |  |  | N.910300 | [5 empty] | BNN-Kennzeichnung: |  |  | N-0117C |  |  |  | ITP 11 | [8 empty] | Name / Name |  |  | Zehner/Moresi/Mehler |  |  |  | Zehner |  |  |  | Zehner
|  |  |  | Order-No.: | [8 empty] | BNN-ID:
|  |  |  | Dok.-Nr.: |  |  | CF0053_0__N-0117C | [5 empty] | CERN-Kennzeichnung: |  |  | HCMB__A001-03000015 | [12 empty] | Firma / Company |  |  | BNN/BNN/BNM |  |  |  | BNN |  |  |  | BNN
|  |  |  | Doc.-ID-No.: | [8 empty] | CERN ID:
|  |  |  | Titel: | Magnetfeldmessung Collared Coil im Warmzustand | [7 empty] | CERN-Freigabe: |  |  | via E-Mail vom | [12 empty] | Datum / Date |  |  | 2002-11-26 |  |  |  | 2002-11-26 |  |  |  | 2002-11-26
|  |  |  | Title: | Warm magnetic measurement collared coil | [7 empty] | CERN release: |  |  | via e-mail dated
Unterschrift / Signature

## Assembly Data
Prog. # cc | Magnet name |  |  | Coil cross-section |  |  | End Spacers
63 | HCMB__A001 | 3000015 |  | 2 |  |  | 1
| COMMENTS: | Measurements before reworking the cold bore of aperture 2
| HOLDING POINT | NA | Data at CERN |  | 2002-12-06 | Analysis by |  | E. Todesco | Answer to MMS-LD |  |  | NA | Answer to manufacturer |  |  | NA
| Shims-summary | [6 empty] | Shims
| Inner average |  |  | Outer average |  |  |  | Aperture 1 |  |  |  |  | Aperture 2
| Used | Nominal | Differ. | Used | Nominal | Differ. |  | Left |  | Right |  |  | Left |  | Right
| 0.2 | 0.2 | 0 | 0.8 | 0.8 | 0 |  | Outer | Inner | Inner | Outer |  | Outer | Inner | Inner | Outer
[8 empty] | 0.8 | 0.2 | 0.2 | 0.8 | Up | 0.8 | 0.2 | 0.2 | 0.8
| Pre-stress (estimate, Mpa) | [6 empty] | 0.8 | 0.2 | 0.2 | 0.8 | Down | 0.8 | 0.2 | 0.2 | 0.8
| Inner average |  |  | Outer average |  |  |  | Seen from conection side
| Used | Nominal | Differ. | Used | Nominal | Differ.
| 75 | 75 | 0 | 75 | 75 | 0
| Peak pre-stress during collaring |  |  |  |  | 110
| Collared coil template - version 11.07.2002 | [8 empty] | Version : |  | cern
1 | Remplir les champs jaunes dans "Assembly Data" et dans "Original Data" | [12 empty] | French
2 | CTRL-g pour charger les fichers des mesures .txt
3 | Sauver le fichier avec un nom different
4 | ALT-F8 et appuyer sur "collared coil analysis" pour analyser les mesures - resultats dans Alarm sheet
1 | Fuellen Sie die gelben Felder in "Assembly Data" und in "Original Data" | [12 empty] | German
2 | CTRL-g um die .txt Messdatensaetze zu laden
3 | Sichern Sie diesen Datensatz mit einem anderen Namen
4 | ALT-F8 und auf "collared coil analysis" druecken, um die Daten zu analysieren => Ergebnis in "Alarm sheet"
1 | Riempire I campi gialli in "Assembly Data" e in "Original Data" | [12 empty] | Italian
2 | CTRL-g per caricare I file .txt delle misure
3 | Salvare il file con un nome diverso
4 | ALT-F8 e premere su "collared coil analysis" per analiszzare le misure - risultati in "Alarm sheet"
1 | Fill in the yellow fields in "Assembly Data" and "Original Data" | [12 empty] | English
2 | CTRL-g to load the .txt files of the measurements
3 | Save the file with a different name
4 | ALT-F8 and press on "collared coil analysis" to analyse the measures - results in Alarm sheet
| Last modif on | by | Modifications:
| 2002-07-10 | E. Todesco | New template with limits for X-section 2

## Difference
File |  |  |  | Difference between _cc and _cca | [17 empty] | File
C1/i (mT/KA) | 3.4118 | -0.11765 | 0 | 0 | 0 | 0 | 0 | 0 | -0.11765 | -0.11765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35294 | 2.2e-05 | C1/i (mT/KA) | -1.6471 | 0 | 0 | 0 | 0 | 0 | 0.11765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.58824
Angle (mrad) | -0.59521 | 0.058896 | 0.31758 | 0.21671 | 0.092419 | 0.089583 | -0.029144 | -0.19567 | -0.12781 | -0.16734 | -0.13353 | 0.22031 | 0.11704 | 0.0812 | -0.2376 | -0.29556 | -0.12566 | 0.02928 | 0.28056 | 0.25224 | -0.12445 | Angle (mrad) | 0.038165 | 0.006819 | 0.39942 | 0.07871 | -0.14651 | -0.081208 | 0.1877 | 0.008829 | -0.17745 | -0.29533 | -0.19961 | -0.067515 | -0.046381 | 0.20198 | 0.46419 | 0.1352 | -0.13371 | -0.14938 | -0.048049 | -0.22515
Multipoles | Position 1 | Position 2 | Position 3 | Position 4 | Position 5 | Position 6 | Position 7 | Position 8 | Position 9 | Position 10 | Position 11 | Position 12 | Position 13 | Position 14 | Position 15 | Position 16 | Position 17 | Position 18 | Position 19 | Position 20 | 0 | Multipoles | Position 1 | Position 2 | Position 3 | Position 4 | Position 5 | Position 6 | Position 7 | Position 8 | Position 9 | Position 10 | Position 11 | Position 12 | Position 13 | Position 14 | Position 15 | Position 16 | Position 17 | Position 18 | Position 19 | Position 20 | 0
b1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | b1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b2 | -0.25393 | -0.016702 | -0.024733 | -0.016927 | -0.011712 | -0.010775 | -0.014757 | -0.016508 | -0.023185 | -0.014278 | -0.020348 | -0.015328 | -0.015255 | -0.014134 | -0.01602 | -0.017668 | -0.020143 | -0.006267 | -0.009535 | -0.012992 | -0.02353 | b2 | -1.0483 | 0.001891 | 0.008253 | 0.017346 | 0.010698 | -0.005826 | 0.023099 | 0.00901 | 0.009056 | 0.01127 | 0.013537 | 0.012766 | 0.016062 | 0.027635 | 0.010776 | 0.013023 | 0.01566 | 0.015535 | 0.009199 | 0.01666
b3 | -1.6454 | 0.0046394 | 0.016221 | -0.0016209 | 0.0056315 | 0.0049824 | 0.007026 | 0.0061019 | 0.0086429 | 0.0025071 | 0.008845 | 0.013832 | 0.013397 | 0.0097321 | 0.01611 | 0.013595 | 0.016518 | 0.026323 | 0.01475 | 0.016591 | -0.033742 | b3 | -0.24402 | 0.010752 | 0.0029975 | 0.010065 | 0.017011 | 0.021341 | 0.010229 | 0.0083904 | 0.0096079 | 0.025383 | 0.006384 | 0.019007 | 0.01149 | 0.008919 | 0.014489 | 0.013229 | 0.011071 | 0.014754 | 0.013015 | 0.023749
b4 | -0.33128 | -4.826e-05 | -0.0028341 | 0.0041261 | 0.0016889 | 4.79e-05 | -0.0018946 | -0.0006418 | 0.0031947 | -0.0015253 | 0.00095753 | -0.002882 | -0.0023627 | -0.0012329 | -8.63e-05 | -0.0032117 | -0.0071749 | -0.0095167 | -0.004212 | 0.0046216 | -0.012342 | b4 | -0.97227 | -0.0001104 | 0.0058037 | 0.0005145 | 0.0042946 | -0.0015609 | 0.0019872 | -0.0022685 | -0.00040769 | 0.0007525 | 0.0013154 | 0.0050392 | -0.001073 | 0.0036104 | -0.0032484 | 0.0027026 | 0.0061286 | -0.0027229 | -0.0023216 | 0.014166
b5 | -0.33697 | 0.002974 | 0.0045945 | 0.0022891 | 0.0028947 | 0.0041659 | 0.0068085 | 0.0039594 | 0.0012312 | -0.0014352 | 0.002028 | 0.0040496 | 0.0014435 | 0.0022539 | 0.0078919 | 0.0030492 | 0.0024781 | 0.0055425 | 0.0026463 | 0.012024 | -0.009028 | b5 | -0.2558 | -0.0007263 | 0.0020289 | 0.000112 | 0.0034276 | -0.0092257 | 0.0020364 | -0.0065773 | -0.0011385 | 0.0034017 | -0.0020951 | 0.0033726 | 0.0051701 | 0.0031721 | 0.0042338 | 0.0015685 | 0.0075013 | 0.0022687 | 0.0021579 | 0.013559
b6 | -0.074992 | 0.0043287 | 0.0021046 | -0.0055827 | -0.0017195 | -0.0051714 | -0.00032375 | 0.0079189 | 0.0080861 | 0.0034543 | 0.0056616 | -0.0019839 | 0.00073972 | -0.0001509 | -0.00071624 | -0.0037258 | -0.0009439 | -0.0023605 | -0.0038518 | 0.0006657 | -0.0021375 | b6 | -0.45502 | -0.0015219 | -0.0053088 | -0.0087145 | -0.0037716 | 0.0049407 | 0.00071829 | 0.023181 | 0.0060759 | 0.0015466 | 0.0019228 | 0.0027414 | -0.0027271 | 0.0016058 | 0.00045006 | 0.0054232 | 0.0047236 | 0.00015558 | 0.0028729 | -0.0046166
b7 | -0.12209 | -0.0048173 | -0.005667 | 0.001314 | -0.000668 | 0.000419 | -0.001017 | -0.00377 | -0.00278 | -0.002253 | -0.001786 | -0.000965 | -0.001728 | -0.000914 | 0.00063 | 0.000203 | -0.000891 | -0.001585 | -0.004521 | -0.001049 | -0.005171 | b7 | -0.084476 | -0.0013074 | -0.0048405 | 0.002865 | -0.003315 | 0.011212 | 0.00384 | -0.00381 | 0.001283 | -0.004303 | -0.003259 | 0.002734 | -0.001969 | -0.0021 | -0.001327 | 0.000252 | 0.000589 | 0.000415 | 0.001734 | 0.0027822
b8 | -0.018763 | -0.0011576 | 0.00094219 | 0.0025655 | 0.00054605 | 0.0038123 | 0.0017764 | 0.0062254 | 0.0082121 | 0.0012832 | 0.0019646 | 0.00043245 | 0.0007536 | -0.001928 | -0.0022656 | -0.0032273 | 0.00045535 | -0.0031671 | -0.0036567 | 0.0014288 | 0.00011544 | b8 | -0.1433 | 0.0047457 | -0.002658 | -0.0046127 | -0.013644 | -0.014849 | -0.010109 | 0.013344 | -7.984e-05 | 0.0047828 | -8.1033e-05 | 0.0026002 | 0.00035478 | 0.0033198 | 0.0011875 | 0.0015342 | -0.00042425 | 0.00027593 | 0.0048291 | -0.0022868
b9 | -0.026603 | 0.0008202 | 0.004512 | 0.00184 | -0.0002309 | 0.0003599 | -0.0010618 | 0.0022297 | 0.0017187 | -0.0008856 | 0.0023077 | 0.0013008 | -0.0005531 | -0.0017599 | -0.0004815 | -0.0014125 | -5.47e-05 | -0.000953 | -0.0028903 | 0.0025587 | -0.0005725 | b9 | -0.025491 | 0.0024422 | 0.0024357 | -0.0004788 | -0.0006618 | -0.012834 | -0.0033305 | -0.001779 | 0.0001075 | 0.0041706 | 0.0028331 | 0.002017 | 0.0013021 | 0.0019877 | -0.0005757 | 0.0005607 | 0.0007734 | 0.0001349 | 0.0015456 | -0.0003817
b10 | 0.00038784 | 0.0070292 | 0.00022886 | -0.0012297 | -0.00021202 | -0.0057705 | -0.0029651 | 0.0021852 | 0.0084884 | 0.0056515 | 0.0010496 | 5.4072e-05 | -0.0021565 | -0.0046179 | -0.00093869 | -0.0017902 | -0.0012508 | -0.003697 | -0.0023292 | 0.0029652 | 0 | b10 | -0.051306 | -0.002104 | -0.0027802 | -0.0062449 | 0.0016854 | 0.0010694 | 0.0010004 | 0.022585 | 0.0029118 | 0.0038549 | -0.0034703 | 0.00093053 | -0.00025127 | 0.0012971 | 0.0011664 | 0.0034534 | 0.0015582 | 0.00028576 | 0.0086467 | -0.0036303
b11 | -0.0061325 | 0.0006611 | -0.0008473 | -0.0004176 | 0.0007239 | -0.0021261 | -0.0005223 | -0.0005611 | -0.0014939 | -0.000226 | -0.0028597 | 0.0012416 | -0.0056836 | -0.00302 | -0.0012878 | -0.0005916 | 0.0004458 | 4.35e-05 | 0.0009859 | 0.0010512 | -0.0010106 | b11 | -0.0094178 | -0.0004047 | -0.0009838 | 0.0004523 | 0.0005764 | 0.0035045 | 0.0010011 | -0.0009294 | 0.0004043 | 3.2e-06 | -0.0026763 | -0.0004855 | 0.0011191 | 0.0032055 | 0.0021669 | 0.0016961 | 0.0001643 | -0.0006436 | 0.0001246 | 0.0008374
b12 | -6.952e-06 | 8.6552e-05 | 0.00030914 | 0.00023012 | 0.00050758 | -0.00076091 | -0.00090391 | 0.00074966 | 0.00072091 | 0.00066297 | -0.00020541 | -0.0015557 | 0.0047166 | 0.0049731 | -0.00013912 | -0.00014979 | -8.814e-05 | 6.8e-06 | -0.00037023 | 0.00062384 | 0.00047456 | b12 | -0.012268 | 0.00094808 | -0.00058629 | -0.0013685 | -0.00085829 | -0.0009794 | -0.00057128 | 0.00088727 | -0.00063932 | -0.00014623 | -0.00032804 | -0.00027807 | -0.0012292 | -0.00037256 | -0.00061044 | -0.00018776 | 0.00010292 | 0.00012165 | 0.00060552 | -0.0016541
b13 | -0.002076 | 6.423e-05 | -0.00024214 | -0.00043871 | 0.00089628 | -0.00046485 | -0.00078273 | 0.00035801 | 6.587e-05 | 6.061e-05 | 0.0013639 | -0.00051575 | 0.0054426 | 0.0032434 | 0.00023678 | 0.001014 | 0.0011286 | 0.00030076 | -0.00010173 | -0.00095805 | 0.0005068 | b13 | -0.00059828 | 0.00034517 | -9.218e-05 | -7.37e-05 | 0.00062966 | -0.00052327 | 0.00041868 | 0.00019967 | 0.00033666 | -0.00016937 | 0.00099751 | -0.0010909 | -0.001235 | -0.0033352 | -0.0013585 | -0.0019977 | -8.659e-05 | -0.00116 | 0.00072971 | 7.871e-05
b14 | 0.00021088 | 2.503e-05 | 0.00017162 | 0.00012352 | 0.00015456 | -0.00067056 | 0.00061283 | -5.6983e-05 | 0.00058006 | -0.00016522 | 0.00034256 | 0.00093454 | -0.0013969 | -0.00081532 | -8.7053e-05 | 0.0014057 | 0.00067968 | 0.00020313 | 0.00017614 | -0.00094383 | 9.3444e-05 | b14 | -0.0035273 | -0.00052646 | 0.00037137 | 0.00027244 | 5.3147e-05 | 0.0005498 | 0.00071135 | 0.00058086 | 0.0003758 | -0.00035711 | 0.00044894 | 0.00081251 | 0.0010438 | -4.8793e-05 | 0.00045593 | -0.00025089 | -0.00067373 | 2.3546e-05 | 0.00011664 | -0.0005189
b15 | 0.00040284 | 0.00072702 | 0.00017019 | 0.00031975 | 0.0004959 | -0.00028726 | 0.00011208 | 0.00014758 | -0.00022129 | -9.323e-05 | 0.00048338 | -0.00032058 | -0.00078387 | 0.00047184 | 0.00082806 | -0.00010974 | -0.00089029 | -0.001341 | 5.9e-06 | -0.00055405 | -3.033e-05 | b15 | -0.001777 | 0.0001063 | -0.00046746 | -0.00060224 | -0.0003662 | -0.00072089 | -0.0003502 | 0.00043796 | -0.00058396 | 2.548e-05 | -0.00039733 | -0.000123 | -0.00018045 | -0.00030272 | -0.00020066 | 0.00017056 | -0.00038044 | 0.00044945 | 0.00024656 | -0.00025759
b16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | b16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | b17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a1 | -5.9523 | 0.58896 | 3.1758 | 2.1671 | 0.92419 | 0.89583 | -0.29144 | -1.9567 | -1.2781 | -1.6734 | -1.3353 | 2.2031 | 1.1704 | 0.81201 | -2.376 | -2.9556 | -1.2566 | 0.2928 | 2.8056 | 2.5224 | 0 | a1 | 0.38166 | 0.068197 | 3.9942 | 0.7871 | -1.4651 | -0.81208 | 1.877 | 0.088293 | -1.7745 | -2.9533 | -1.9961 | -0.67515 | -0.46381 | 2.0198 | 4.6419 | 1.352 | -1.3371 | -1.4938 | -0.48049 | -2.2515
a2 | 2.3721 | 0.0035439 | 0.0022923 | 0.0044824 | 0.0085195 | -0.000863 | -0.0039543 | -0.0001399 | 0.012056 | -0.0039882 | -0.003607 | 0.010119 | 0.0098846 | -0.015583 | -0.013293 | 0.010101 | 0.0088381 | -0.005177 | -0.015595 | 0.011034 | 0.079234 | a2 | 4.9037 | 0.011236 | 0.00873 | -0.019781 | -0.005117 | -0.01302 | -0.000443 | 0.016482 | 0.001437 | -0.035175 | -0.021301 | -0.001411 | 0.002056 | -0.020314 | -0.00123 | 0.005332 | -0.005269 | 0.0040138 | -0.0046112 | -0.002627
a3 | -0.38729 | -0.0025868 | 0.0073199 | 0.0005865 | -0.0029024 | 0.0033346 | -0.0027703 | -0.0026841 | -0.0042408 | -0.0026817 | 0.0020014 | -0.0039591 | 9.18e-05 | -0.0063891 | -0.002666 | -0.00090178 | -0.0015263 | -0.004217 | -0.0046785 | -0.0006775 | -0.015046 | a3 | 0.41511 | 0.0082626 | -0.0020085 | -0.0035741 | -0.0019532 | 0.003247 | 0.003506 | 0.0027641 | -0.0001365 | 0.01008 | 0.0014435 | 0.0035387 | 0.0043331 | 0.0017611 | 0.0060259 | 0.0065449 | 0.0038464 | 0.0022238 | 0.0020204 | 0.0027003
a4 | 0.64665 | -0.0029064 | 0.0038327 | 0.0020401 | -0.0017206 | -0.0067202 | -0.0022358 | -0.0042076 | 0.0062131 | -0.0025265 | 0.0009572 | 0.0056341 | 0.0032634 | -0.0007385 | 0.0028925 | 0.0039699 | 0.0058577 | -0.0018893 | -0.0024734 | -0.0086373 | 0.021962 | a4 | 1.3881 | -0.0005335 | -0.0010865 | -0.0062619 | -0.0021109 | 0.0087009 | -0.0025949 | -0.0015309 | -0.0029964 | -0.0021307 | -9.57e-05 | 0.0039458 | 0.0062703 | -0.004927 | -0.0029367 | -0.0018877 | -0.0009836 | -0.0016225 | 0.0021531 | 0.020185
a5 | -0.19352 | -0.0034171 | -0.0059064 | -0.0032849 | -0.0023534 | -0.00037595 | -0.0026571 | -0.0065875 | 0.0007822 | -0.0011558 | 6.889e-05 | 0.0041764 | 0.00068026 | 0.00077186 | 0.00030753 | -0.0024339 | 0.00012731 | -0.0005496 | -0.004768 | -0.018098 | -0.0077436 | a5 | 0.10637 | -0.0066905 | 0.0030729 | -0.0022517 | -0.0010065 | 0.00024895 | 0.0045289 | 0.0060389 | -0.0041587 | 0.00477 | 0.0004877 | -0.00087646 | -0.0003079 | -0.0019006 | -0.0017146 | 0.0014146 | -0.0025706 | -0.004535 | 0.0006618 | -0.0061207
a6 | 0.17286 | -0.002336 | 0.0046791 | 0.0013731 | 0.004601 | 0.003892 | 0.0043435 | -0.0067199 | 0.01454 | -0.0023761 | -0.0020533 | 0.0005479 | 0.0057607 | -0.0044991 | -0.0039666 | 0.0001243 | 0.0049298 | 0.0047152 | -0.0032207 | 0.0046282 | 0.0071453 | a6 | 0.37882 | -0.0030944 | -0.0027729 | -0.0010816 | -0.0007946 | -0.0004216 | 0.0015917 | 0.0068101 | 0.0027755 | -0.0074764 | 0.0088949 | 0.004247 | 0.0005856 | -0.0030362 | 0.0012875 | 0.002697 | -0.0037911 | 0.0005439 | -0.0020674 | -0.0049213
a7 | -0.10879 | -0.0054188 | 0.0011061 | 0.005573 | 0.0046722 | 0.010479 | 0.004376 | -0.0041161 | 0.0021918 | 0.00032968 | 0.0011592 | 0.0052254 | 0.0035927 | 0.0012863 | -0.0011928 | 5.786e-05 | 0.0018085 | 0.0031155 | 0.0042816 | 0.0017809 | -0.0011209 | a7 | 0.002185 | 0.00075237 | -0.0037582 | -0.0076478 | -0.01258 | -0.00776 | -0.0049835 | -0.00023219 | 0.00085022 | -0.0063234 | -0.0013686 | -0.0017468 | 0.001253 | -0.00097897 | 0.0071325 | 0.0012364 | 0.0001657 | -0.00071519 | 0.006218 | 0.0026232
a8 | 0.017786 | -0.00097348 | -0.00061242 | -0.0057458 | -0.0092515 | -0.010608 | -0.017876 | -0.004854 | 0.0071166 | -0.0059716 | 0.00019515 | -0.00086773 | 0.002774 | -0.0039465 | -0.0036687 | 3.858e-05 | 4.156e-05 | -0.002264 | -0.0044364 | 0.004751 | -0.0024242 | a8 | 0.056808 | 0.0032335 | 0.0037209 | 0.0066014 | 0.013809 | 0.0045389 | -0.002885 | 0.0074568 | 0.0040743 | 0.0016392 | 0.0034475 | 0.00047428 | -0.00023751 | -9.604e-05 | 0.00012619 | 0.0028798 | -0.0026049 | -0.00074143 | -0.0039994 | -0.00074199
a9 | -0.02116 | 0.0057747 | 0.0047492 | -0.00087145 | -0.0033062 | -0.0079589 | -0.0088364 | 0.0022206 | -0.00133 | 0.0015666 | 0.0027157 | 0.0034218 | -7.761e-05 | 0.0022281 | 0.00074693 | -0.00048136 | -7.473e-05 | 3.682e-05 | 0.0023816 | 0.0048359 | -0.00047691 | a9 | -0.011563 | 0.00040222 | 0.0060836 | 0.0062462 | 0.012427 | 0.008194 | 0.0058852 | 0.0034103 | 0.00048917 | 0.0052229 | 0.0011985 | 0.0011586 | 0.0016796 | 0.0030527 | 0.0021621 | 0.0024728 | -0.00076954 | -0.0023079 | 0.0012254 | 0.0030879
a10 | 0.011017 | -0.0050333 | 0.0024497 | -0.0056455 | 0.0061365 | 0.0085563 | 0.0017831 | -0.00037241 | 0.010181 | 0.0017349 | -0.006126 | 0.0021837 | 0.005355 | -0.010624 | -0.0087669 | -0.0018133 | -0.0024276 | -0.0005771 | -0.0088622 | 0.0079044 | 0 | a10 | 0.014123 | -0.00010808 | -0.005014 | -0.0015418 | -0.0052524 | -0.0019205 | 0.0084764 | 0.002084 | 0.0018579 | -0.00065204 | 0.011954 | -0.00066501 | 0.0017811 | -0.0030005 | -0.0011846 | 0.00096782 | -0.0055161 | -0.0016791 | -0.0057907 | -0.0056892
a11 | -0.012269 | 0.00025398 | 0.0053959 | 0.0048764 | 0.0029016 | 0.0036231 | 0.00024633 | 0.00033345 | 0.0021233 | 0.0021262 | 0.0018085 | 0.0067222 | 0.0044244 | 0.004288 | -0.00032739 | -0.0004638 | 0.0003049 | 0.0019143 | 0.0044933 | 0.0059727 | 0.0021885 | a11 | -0.006401 | 0.0009262 | 0.0039267 | 1.57e-05 | -0.0022815 | 0.00083316 | 0.004017 | -0.00024475 | -0.0010228 | -0.0056383 | -0.0020752 | -0.00050206 | -0.00061336 | 0.0013375 | 0.0057412 | 0.0022606 | -0.00087578 | -0.00033711 | 0.00091298 | -0.00099546
a12 | 0.00097273 | -0.0018196 | -1.8675e-05 | -0.00023364 | -0.00087494 | -0.00027384 | -0.00072833 | -0.00035413 | 0.0020868 | 0.0008346 | -0.0017974 | -0.00024075 | -9.3916e-05 | -0.0056685 | 0.00052758 | 0.00094998 | 0.0011452 | -0.00077416 | -0.0015822 | 0.00025826 | -0.00042405 | a12 | -0.00033019 | 0.0014873 | 0.00017317 | -0.00083156 | 0.00038404 | -0.0010695 | 0.00039707 | 0.0013109 | 0.00059276 | -0.00082681 | 0.00024515 | -0.001458 | -0.00056808 | -0.0023273 | -0.0008769 | -0.0018728 | -0.0010244 | -0.00052967 | -0.00029591 | 0.0013547
a13 | -0.0019657 | -0.00089483 | 0.0012359 | 0.00060799 | 0.00011309 | 0.00088234 | -0.00070553 | -0.00078531 | -0.00016042 | -0.00032011 | -0.002109 | -0.00080429 | -0.0018348 | -0.0032775 | -3.6394e-05 | 0.0012468 | 0.00018323 | -8.9021e-05 | 0.00082032 | 0.00069247 | -0.00035669 | a13 | -0.0014141 | 0.0001178 | 0.0013985 | -0.00082782 | 0.00081427 | -0.00039448 | 0.00023554 | 0.00019877 | -0.0003623 | -0.00046413 | 0.00033915 | -0.00033829 | 0.0015813 | 0.00042026 | -0.00070993 | 0.00019061 | -0.0010031 | 0.00013165 | -0.00031892 | 0.00032934
a14 | 4.5745e-05 | -0.0005116 | 0.00086946 | -0.00050868 | 0.00037286 | 0.00053536 | 0.00012658 | -0.0012757 | 0.00057309 | -0.00031553 | -0.00013214 | 0.00060343 | 0.0013896 | 0.0010597 | -0.0010617 | 7.802e-05 | 3.8478e-05 | -0.00013747 | -0.00054845 | 0.00051071 | 8.2527e-05 | a14 | -0.0039235 | 0.00039152 | -0.00031674 | -0.0001764 | -0.0010306 | -3.713e-05 | -0.00026708 | 1.6409e-05 | -4.1216e-05 | 5.6539e-05 | 0.00016396 | 7.174e-05 | 0.00099498 | 0.00035853 | 0.00019815 | 0.00096548 | 1.665e-05 | -0.00040702 | -0.00081086 | 0.00096025
a15 | -0.00016179 | 0.0002407 | 0.00087586 | 0.00030553 | -0.0004211 | -0.00012853 | -7.667e-05 | 0.00029901 | 0.0010632 | 8.6365e-05 | 8.1941e-05 | -0.00036693 | 5.2959e-05 | -0.00095955 | -0.00056142 | -0.00033106 | -5.9441e-05 | 0.0004537 | -0.00052418 | 0.0011338 | 3.6302e-05 | a15 | -0.00073723 | -8.764e-06 | 0.00063315 | -5.034e-05 | 9.48e-06 | 0.00027483 | 0.00026273 | 0.0012225 | -0.00011279 | 0.00015844 | -0.00058862 | -0.00049058 | -0.00042214 | 4.415e-05 | 0.00030148 | 0.00013796 | 0.0001833 | 0.00037272 | 0.00010009 | -0.00013572
a16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dx (mm) | 0.0093388 | 0.016427 | 0.00027914 | -0.0008493 | -0.0016244 | 0 | -0.0066869 | 0.0048554 | 0.017169 | 0.012225 | 0.0035507 | 0.00024519 | -0.0061265 | -0.0092545 | -0.00031088 | -0.0036163 | -0.0020592 | -0.0080657 | -0.0034983 | 0.0058503 | 0 | Dx (mm) | -0.11259 | -0.0042612 | -0.0049328 | -0.013408 | 0.0048367 | 0.0031614 | 0.0010436 | 0.049583 | 0.0062985 | 0.0089385 | -0.0088015 | 0.0021525 | -0.00090409 | 0.0036481 | 0.0020894 | 0 | 0.0046359 | 0.00079633 | 0.020126 | -0.0075914
Dy (mm) | 0.026239 | -0.0095926 | 0.0057135 | -0.013897 | 0.01306 | 0.018069 | 0.0033737 | -0.00055522 | 0.023456 | 0.0122 | 0 | 0.0046222 | 0.019893 | -0.023082 | -0.019572 | 0 | -0.005566 | 0 | -0.019535 | 0.028208 | 0 | Dy (mm) | 0.072527 | -0.00098164 | -0.011416 | -0.0046182 | -0.011523 | -0.0036266 | 0.019041 | 0 | 0.0044607 | -0.001429 | 0.02601 | -0.0012204 | 0.0040485 | -0.0056619 | -0.0019555 | 0.0030173 | -0.010786 | -0.0036425 | -0.011178 | -0.015019
Mag. len. (m) | 0.004978 | [20 empty] | Mag. len. (m) | -0.001297
TF (mT/KA) | -0.019608 | [20 empty] | TF (mT/KA) | 0.0065359
Coil pos. (mm) | -0.00011511 | [20 empty] | Coil pos. (mm) | -3.9092e-06
Current (A) | 0 | [20 empty] | Current (A) | 0

## Summary Data
File | HCMB__A001-3000015 |  |  | Aperture 1 - Collared coils | [16 empty] | Integrals | File | HCMB__A001-3000015 |  |  | Aperture 2 - Collared coils | [16 empty] | Integrals
C1/i (mT/KA) | 379.7647 | 596.5882 | 596.1176 | 596.2353 | 596.1176 | 596.1176 | 596.2353 | 596.2353 | 596.2353 | 596.1176 | 596.1176 | 596.2353 | 596.1176 | 596.2353 | 596.1176 | 596.2353 | 596.1176 | 596.2353 | 596.5882 | 382.5882 | 0.073267 | C1/i (mT/KA) | 383.0588 | 596.4706 | 596.2353 | 596.2353 | 596.1176 | 596.2353 | 596.2353 | 596.1176 | 596.2353 | 596.2353 | 596.3529 | 596.2353 | 596.2353 | 596.2353 | 596.2353 | 596.2353 | 596.2353 | 596.2353 | 596.7059 | 382 | 0.07329
Angle (mrad) | 5.0455 | -0.28366 | -0.99624 | -1.4006 | -1.1345 | -0.86363 | -0.28741 | 0.8436 | 0.98871 | 0.68847 | 0.29679 | 0.50213 | 0.39834 | 0.45756 | 0.29501 | -0.25994 | -0.59808 | -0.43064 | -0.88079 | -0.93303 | 3.9413 | Angle (mrad) | 4.6056 | -0.11916 | -1.0264 | -1.2498 | -0.76816 | -0.66277 | -0.18648 | 0.59425 | 0.91275 | 0.42992 | 0.37603 | 0.50802 | 0.52609 | 0.6003 | -0.086677 | -0.32122 | -0.76546 | -0.46679 | -0.49312 | -1.1204 | 3.9288
Multipoles | Position 1 | Position 2 | Position 3 | Position 4 | Position 5 | Position 6 | Position 7 | Position 8 | Position 9 | Position 10 | Position 11 | Position 12 | Position 13 | Position 14 | Position 15 | Position 16 | Position 17 | Position 18 | Position 19 | Position 20 | 0 | Multipoles | Position 1 | Position 2 | Position 3 | Position 4 | Position 5 | Position 6 | Position 7 | Position 8 | Position 9 | Position 10 | Position 11 | Position 12 | Position 13 | Position 14 | Position 15 | Position 16 | Position 17 | Position 18 | Position 19 | Position 20 | 0
b1 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | b1 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000 | 10000
b2 | -1.1065 | -1.8643 | -1.7945 | -2.0648 | -1.6547 | -1.2586 | -1.9746 | -2.0602 | -2.0482 | -0.72977 | -2.1074 | -1.5987 | -1.2147 | -1.1209 | -1.4765 | -1.2707 | -0.10583 | -1.4567 | -2.1294 | -2.2993 | -1.5619 | b2 | 3.6742 | 1.3618 | 1.648 | 1.6861 | 1.9797 | 2.9188 | 2.3245 | 2.9294 | 2.5089 | 1.6461 | 1.2312 | 1.9397 | 2.0319 | 1.6446 | 0.66546 | 1.6635 | 1.1066 | 1.2006 | 1.8597 | 1.2941 | 1.8428
b3 | 36.9244 | -0.51148 | -0.16674 | 0.17874 | -0.13966 | -0.35273 | 1.0182 | 0.054169 | 0.057326 | 0.21665 | -0.010198 | -0.5176 | -0.076344 | -0.89824 | -0.14094 | -0.01924 | 0.41097 | -0.49749 | -0.36958 | -0.72082 | 1.1044 | b3 | 35.848 | -0.96252 | -0.81068 | -0.47497 | -0.32193 | -1.7279 | 0.46052 | -0.40835 | -0.35097 | -0.78394 | -1.138 | -1.3588 | -0.45723 | -1.1551 | -0.55109 | 0.58845 | 0.78626 | -0.85738 | -0.022038 | -0.76617 | 0.67376
b4 | -0.071183 | 0.051785 | 0.12911 | -0.12728 | -0.10815 | -0.13811 | -0.13824 | -0.15086 | 0.010011 | 0.088925 | -0.060551 | 0.16825 | 0.053965 | -0.18394 | -0.24464 | -0.08641 | -0.00091216 | 0.13888 | -0.15254 | -0.50037 | -0.057948 | b4 | 0.10494 | -0.10124 | 0.22671 | 0.27296 | 0.49378 | 0.17791 | 0.3348 | 0.085569 | 0.064158 | 0.48212 | 0.38035 | 0.20093 | 0.36511 | 0.084708 | -0.032569 | 0.081259 | -0.15731 | -0.26304 | 0.19207 | -0.14382 | 0.1485
b5 | -3.6812 | 0.019171 | -0.30337 | 0.14568 | 0.13917 | 0.35254 | 0.228 | 0.34477 | 0.20091 | 0.34547 | 0.68705 | 0.22858 | 0.27386 | 0.54483 | 0.25188 | 0.23531 | 0.040419 | 0.24215 | 0.1418 | -3.4566 | -0.023051 | b5 | -4.4252 | -0.44308 | -0.27541 | -0.24357 | -0.28755 | 0.040316 | -0.10963 | 0.22786 | 0.034885 | -0.38266 | 0.15541 | 0.0093049 | -0.17104 | 0.18079 | -0.058396 | 0.089298 | -0.0016341 | 0.038882 | -0.11821 | -3.6159 | -0.33574
b6 | 0.16583 | 0.1376 | 0.090193 | 0.080947 | -0.015888 | -0.08443 | 0.08685 | 0.11888 | 0.029652 | -0.12615 | 0.080442 | 0.1279 | 0.0077351 | -0.14314 | -0.041878 | -0.0024439 | -0.026296 | 0.041599 | 0.044464 | -0.020754 | 0.025856 | b6 | 0.36798 | 0.12293 | 0.076544 | 0.04192 | -0.047099 | -0.3296 | -0.056453 | -0.15208 | -0.12872 | -0.0025041 | 0.12646 | -0.14529 | 0.068379 | 0.00056698 | 0.030631 | 0.011938 | -0.032782 | 0.034583 | 0.15182 | -0.045865 | -0.0011148
b7 | 2.9665 | 0.95309 | 1.0884 | 1.1695 | 1.1205 | 1.115 | 1.067 | 1.1308 | 1.1617 | 1.0902 | 1.0695 | 1.1183 | 1.1568 | 1.1002 | 1.1448 | 1.2039 | 1.1783 | 1.2409 | 1.1748 | 0.77977 | 1.1761 | b7 | 2.8678 | 0.93392 | 0.98059 | 1.0645 | 1.0914 | 0.9665 | 1.0373 | 1.1872 | 1.1607 | 1.0631 | 1.0464 | 1.0621 | 1.1016 | 1.1046 | 1.0495 | 1.1397 | 1.1251 | 1.1261 | 1.0442 | 0.76894 | 1.1212
b8 | -0.030943 | 0.08221 | 0.0044636 | 0.035683 | 0.010738 | -0.00049327 | -0.0022855 | -0.040196 | 0.0040277 | -0.0037244 | 0.0022393 | 0.0065824 | 0.0036627 | 0.048358 | 0.0093122 | 0.020134 | -0.037869 | -0.039497 | -0.023856 | 0.019434 | 0.0037483 | b8 | 0.070148 | 0.074678 | 0.045808 | -0.0012362 | -0.074507 | -0.035044 | -0.050681 | -0.077474 | -0.063725 | -0.068154 | -0.0086611 | -0.024193 | -0.00051476 | -0.050522 | -0.029019 | 0.0081077 | -0.0058195 | -0.052662 | 0.012183 | -0.0030947 | -0.01858
b9 | 0.41748 | 0.48033 | 0.47543 | 0.49639 | 0.48646 | 0.47147 | 0.48176 | 0.46554 | 0.46736 | 0.48209 | 0.46702 | 0.47194 | 0.48727 | 0.48244 | 0.49074 | 0.49499 | 0.50595 | 0.50598 | 0.48864 | 0.45493 | 0.48031 | b9 | 0.40953 | 0.50185 | 0.46583 | 0.46086 | 0.47877 | 0.49299 | 0.49794 | 0.49976 | 0.49546 | 0.47507 | 0.48378 | 0.47866 | 0.48822 | 0.47122 | 0.44244 | 0.45232 | 0.47597 | 0.48097 | 0.47231 | 0.42978 | 0.47466
b10 | 0.023821 | 0.079762 | -0.0027221 | 0.091372 | 0.04863 | 0.0054363 | 0.075746 | 0.034913 | 0.019205 | -0.029158 | 0.049485 | 0.0085797 | -0.029362 | -0.1005 | -0.015398 | -0.023901 | -0.091713 | -0.077417 | -0.038352 | -0.030889 | 0 | b10 | 0.15019 | 0.18374 | -0.017043 | 0.021284 | -0.029485 | -0.052822 | -0.019017 | -0.10242 | -0.045952 | -0.047526 | 0.10773 | 0.02662 | 0.027456 | -0.067634 | -0.016313 | -0.0037556 | -0.015409 | -0.03852 | 0.019275 | -0.041861 | 0
b11 | 0.65413 | 0.76241 | 0.75184 | 0.76288 | 0.76506 | 0.77742 | 0.77114 | 0.77666 | 0.76717 | 0.76579 | 0.77845 | 0.76865 | 0.77112 | 0.77935 | 0.76979 | 0.7656 | 0.7631 | 0.76944 | 0.76212 | 0.68334 | 0.76163 | b11 | 0.65105 | 0.76654 | 0.76278 | 0.76737 | 0.75856 | 0.77901 | 0.76646 | 0.76226 | 0.75913 | 0.76814 | 0.78574 | 0.77834 | 0.76729 | 0.76654 | 0.76765 | 0.75872 | 0.75977 | 0.7652 | 0.76987 | 0.6852 | 0.76059
b12 | -0.0078914 | 0.0032538 | -0.0066675 | 0.0071259 | 0.0053677 | -0.0020543 | 0.0032101 | -0.0046778 | 0.00016275 | -0.0032812 | 0.00069595 | -0.0034372 | -0.00099686 | -0.0026816 | 0.0041627 | -0.0032112 | -0.011544 | -0.013591 | -0.004012 | 0.00076481 | -0.001904 | b12 | 0.028899 | 0.023122 | 0.00078119 | 0.0012049 | 0.0014174 | 0.0092032 | 0.0055472 | -0.002776 | 0.00123 | 0.0034077 | 0.015501 | 0.0099268 | 0.0097503 | -0.0078054 | 0.00021061 | 0.00084608 | 0.0036288 | -0.0012842 | 0.0037075 | -0.0074219 | 0.004742
b13 | 0.088954 | 0.070811 | 0.075979 | 0.070949 | 0.068208 | 0.069577 | 0.069658 | 0.070105 | 0.070429 | 0.068681 | 0.064828 | 0.071512 | 0.071989 | 0.066743 | 0.069738 | 0.072042 | 0.072658 | 0.071323 | 0.072591 | 0.053167 | 0.070472 | b13 | 0.088535 | 0.07378 | 0.071784 | 0.069506 | 0.070308 | 0.061328 | 0.064644 | 0.065548 | 0.065266 | 0.069041 | 0.061628 | 0.06485 | 0.068613 | 0.065543 | 0.067437 | 0.070196 | 0.069565 | 0.069266 | 0.07085 | 0.052866 | 0.06793
b14 | 0.0032961 | -0.0029784 | -0.0068003 | -0.002143 | -0.0036416 | -0.0057197 | -0.0039016 | -0.0050413 | -0.0047105 | -0.0072273 | -0.0046932 | -0.0079761 | -0.0070089 | -0.010884 | -0.0064117 | -0.0076817 | -0.0085923 | -0.0086893 | -0.0075185 | -0.0032447 | -0.0057886 | b14 | 0.0015905 | 0.0041546 | -0.009027 | -0.0076941 | -0.0075516 | -0.0080452 | -0.0072209 | -0.010326 | -0.0086822 | -0.0066076 | -0.00035296 | -0.0046911 | -0.0037288 | -0.0093413 | -0.0076468 | -0.006718 | -0.0059998 | -0.0067553 | -0.0052339 | -0.0050206 | -0.0058942
b15 | -0.0080025 | 0.031109 | 0.024468 | 0.026128 | 0.026214 | 0.02528 | 0.027842 | 0.02783 | 0.027706 | 0.024335 | 0.029308 | 0.027432 | 0.026013 | 0.025787 | 0.027475 | 0.023806 | 0.01874 | 0.022943 | 0.024944 | 0.0061476 | 0.024183 | b15 | -0.010775 | 0.028991 | 0.026886 | 0.027223 | 0.022958 | 0.024678 | 0.024136 | 0.022345 | 0.024472 | 0.022749 | 0.028569 | 0.027043 | 0.027809 | 0.025083 | 0.026714 | 0.025966 | 0.023126 | 0.022071 | 0.025031 | 0.0031618 | 0.023386
b16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | b16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | b17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a1 | 50.4555 | -2.8366 | -9.9624 | -14.0055 | -11.3446 | -8.6363 | -2.8741 | 8.436 | 9.8871 | 6.8847 | 2.9679 | 5.0213 | 3.9834 | 4.5756 | 2.9501 | -2.5994 | -5.9808 | -4.3064 | -8.8079 | -9.3303 | 0 | a1 | 46.0564 | -1.1916 | -10.2643 | -12.4982 | -7.6815 | -6.6277 | -1.8648 | 5.9425 | 9.1275 | 4.2992 | 3.7603 | 5.0802 | 5.2609 | 6.003 | -0.86677 | -3.2122 | -7.6546 | -4.6679 | -4.9312 | -11.2041 | 0
a2 | -2.2543 | -0.5225 | -0.40533 | -0.20809 | 0.84523 | -0.47805 | -0.75909 | -0.78825 | 0.038656 | -0.14885 | 1.0404 | 0.44199 | -0.90635 | -0.15107 | -0.7941 | -0.23114 | -0.58939 | -0.016584 | -0.22082 | -0.091552 | -0.27742 | a2 | -0.050569 | -2.0627 | -2.3266 | -3.5006 | -2.7698 | -0.79251 | -1.822 | -2.9709 | -3.1933 | -0.94332 | -0.94807 | -1.9975 | -2.2265 | -1.6409 | -1.0989 | -1.6136 | -1.8887 | -0.45239 | -0.67103 | 6.1749 | -1.5036
a3 | -1.5768 | 0.92985 | 0.58326 | 0.56756 | 0.37085 | 0.0060813 | 0.26901 | 0.50621 | 0.94619 | 0.62702 | 0.25382 | 0.7205 | 0.33254 | 0.16496 | 0.23149 | 0.069836 | 0.82219 | 1.0315 | 0.50846 | 0.13656 | 0.41627 | a3 | 0.65035 | 0.58533 | 0.48578 | 0.61176 | 0.78206 | 1.1065 | 0.91963 | 0.67583 | 0.47622 | 0.3553 | 0.33936 | 0.76036 | 0.6855 | 0.8232 | 0.053931 | -0.051754 | 0.035004 | 0.68925 | -0.243 | 0.58866 | 0.5126
a4 | 0.66837 | -0.27018 | -0.31872 | -0.14226 | -0.25155 | -0.58669 | -0.30961 | -0.083621 | -0.10392 | -0.38742 | -0.13162 | 0.019514 | -0.0031355 | -0.13523 | 0.56506 | 0.31048 | -0.11966 | 0.14284 | 0.017552 | -0.3592 | -0.082625 | a4 | 0.21335 | 0.21805 | -0.15458 | -0.065272 | 0.036673 | -0.48743 | 0.24741 | 0.1301 | 0.10738 | 0.27603 | 0.28072 | -0.14308 | 0.018238 | -0.54329 | 0.26997 | 0.29912 | 0.40652 | -0.066867 | 0.23731 | 0.55461 | 0.080879
a5 | 2.4262 | 0.17163 | 0.10768 | 0.010103 | 0.021734 | 0.0041218 | 0.13352 | 0.1294 | 0.2473 | -0.038951 | 0.018569 | 0.14921 | 0.0064507 | 0.098284 | -0.087886 | -0.035881 | -0.01623 | 0.12026 | -0.07067 | -0.24564 | 0.12222 | a5 | 3.2786 | 0.080686 | -0.0010536 | 0.010542 | -0.25821 | -0.036086 | -0.09996 | -0.1037 | -0.12133 | -0.21156 | -0.1741 | -0.077797 | -0.27683 | -0.090354 | -0.1402 | -0.13556 | -0.092718 | -0.11669 | -0.14913 | 0.092605 | 0.008901
a6 | -0.011446 | -0.14094 | 0.0090321 | 0.10249 | 0.090952 | -0.021179 | -0.088369 | 0.016769 | 0.074988 | 0.15859 | 0.2923 | 0.14407 | 0.13761 | 0.16329 | 0.12787 | 0.1306 | 0.095813 | 0.11313 | 0.039413 | -0.083354 | 0.071867 | a6 | 0.27602 | 0.051468 | 0.10945 | -0.010856 | 0.1861 | 0.36578 | 0.24699 | 0.26729 | 0.29582 | 0.25318 | 0.39535 | 0.29583 | 0.18769 | 0.089836 | 0.056289 | 0.030133 | -0.038091 | 0.12212 | 0.14687 | 0.31205 | 0.1778
a7 | 1.4746 | -0.071754 | -0.070866 | -0.074172 | -0.05805 | -0.0065121 | -0.074437 | -0.05896 | -0.03751 | -0.010458 | 0.03708 | 0.023431 | -0.049783 | -0.058515 | -0.092783 | -0.054597 | -0.090285 | -0.013444 | -0.0556 | 0.039553 | 0.0076647 | a7 | 1.7391 | -0.057963 | -0.05468 | -0.08427 | -0.14095 | -0.12407 | -0.085089 | -0.049335 | -0.066197 | -0.12943 | -0.0708 | -0.091141 | -0.035322 | 0.046709 | -0.071858 | -0.099677 | -0.11289 | 0.045054 | -0.034697 | 0.044182 | -0.0037035
a8 | 0.009668 | 0.012118 | 0.080493 | 0.084749 | 0.047205 | 0.04972 | 0.068499 | 0.068447 | 0.055011 | 0.075783 | 0.075837 | 0.080649 | 0.048454 | 0.058756 | 0.027073 | 0.077271 | 0.093345 | 0.069918 | 0.031025 | 0.0031091 | 0.057705 | a8 | -0.027275 | 0.043649 | 0.0044839 | -0.0099936 | -0.0025449 | -0.090524 | 0.025037 | 0.019019 | 0.036054 | -0.046538 | -0.010401 | -0.014289 | -0.026167 | -0.024859 | -0.048134 | -0.037773 | -0.013686 | -0.0065048 | -0.03867 | 0.0084436 | -0.013169
a9 | -0.30846 | -0.047977 | -0.040823 | -0.033042 | -0.045504 | 0.0051514 | 0.0072831 | -0.039137 | -0.03926 | -0.017796 | -0.026643 | -0.022201 | -0.039865 | -0.024966 | -0.018145 | -0.024263 | -0.041144 | -0.025798 | -0.054533 | -0.090711 | -0.040622 | a9 | -0.1788 | 0.001407 | -0.01211 | -0.040234 | -0.057542 | -0.058653 | -0.015163 | 0.0060433 | -0.017623 | -0.021861 | -0.018258 | -0.0079532 | -0.012596 | -0.049435 | -0.066311 | -0.037132 | -0.046486 | -0.05334 | -0.024515 | -0.084264 | -0.036341
a10 | -0.048571 | -0.030957 | 0.022433 | 0.022704 | 0.0055727 | 0.032297 | 0.015037 | -0.028274 | -0.035715 | 0.0053697 | -0.0011175 | 0.023455 | 0.0060669 | -0.02142 | -0.039653 | 0.00027294 | 0.053177 | 0.0035286 | -0.0055389 | 0.0058084 | 0 | a10 | 0.077972 | 0.019965 | 0.018356 | -0.052821 | 0.021206 | -0.0061805 | 0.016292 | 0.0054906 | -0.0081716 | -0.013995 | 0.0014852 | 0.012167 | -0.038452 | -0.050108 | -0.043384 | -0.046364 | 0.0063387 | 0.040905 | 0.047863 | 0.030073 | 0
a11 | 0.14866 | -0.078374 | -0.081958 | -0.078284 | -0.070032 | -0.053641 | -0.061926 | -0.054623 | -0.053238 | -0.053695 | -0.050091 | -0.05939 | -0.0629 | -0.066391 | -0.069425 | -0.06916 | -0.075476 | -0.061989 | -0.070753 | -0.06177 | -0.057882 | a11 | 0.17767 | -0.075861 | -0.07978 | -0.073721 | -0.072479 | -0.080509 | -0.060355 | -0.053244 | -0.050447 | -0.060385 | -0.056137 | -0.064082 | -0.059014 | -0.05084 | -0.072353 | -0.067959 | -0.072619 | -0.058326 | -0.06401 | -0.061925 | -0.056942
a12 | -0.013036 | -0.010223 | -0.0018041 | -0.0042869 | -0.0033459 | -0.0074111 | -0.0072388 | -0.0083867 | -0.0078713 | -0.0059329 | 0.0065399 | 0.00093021 | -0.0019734 | -0.0049661 | -0.0093697 | -0.0051654 | 0.0025303 | -0.00096504 | -0.001047 | -0.0034265 | -0.0041753 | a12 | 0.0022276 | -0.0015296 | 0.002154 | -0.010785 | 0.0040001 | 0.010067 | 0.00088579 | 0.00076003 | 0.001642 | 0.0004408 | 0.0087888 | 0.0066019 | -0.00082903 | 0.004461 | -0.001665 | -0.0044703 | -0.0031448 | 0.0059709 | 0.0074523 | 0.0037063 | 0.0017948
a13 | -0.027618 | -0.0041321 | -0.0054115 | -0.0068115 | -0.0062593 | -0.0030203 | -0.0040482 | -0.0043036 | -0.0019716 | -0.0011869 | -0.0029345 | -0.0019382 | -0.0028604 | -3.9574e-05 | -0.0074154 | -0.0079031 | -0.0064563 | -0.0022933 | -0.0069987 | -0.0061182 | -0.0050552 | a13 | -0.016507 | -0.0068934 | -0.0060293 | -0.0081294 | -0.009749 | -0.0062491 | -0.0036494 | -0.0025686 | -0.004466 | -0.0066619 | -0.0056262 | -0.0056716 | -0.0069785 | -0.0025555 | -0.0074111 | -0.0094721 | -0.0092736 | -0.0085665 | -0.0073538 | -0.0065962 | -0.0068543
a14 | 0.0055147 | -0.0092073 | -0.0068393 | -0.0086593 | -0.0093791 | -0.0081214 | -0.0081685 | -0.0082302 | -0.0075749 | -0.0084622 | -0.0099922 | -0.0094641 | -0.0099143 | -0.0095295 | -0.010172 | -0.0064507 | -0.0036561 | -0.0050551 | -0.0068489 | -0.003601 | -0.0074968 | a14 | 0.0047681 | -0.0045201 | -0.0058854 | -0.0071797 | -0.0028866 | -0.0098619 | -0.0059232 | -0.0051436 | -0.0036837 | -0.004952 | -0.0071325 | -0.0058456 | -0.0074757 | -0.008593 | -0.0056153 | -0.0055336 | -0.0010731 | -0.0037307 | -0.0040847 | -0.00095995 | -0.0050131
a15 | 0.0010005 | -0.0042833 | -0.0073064 | -0.0036715 | -0.0044666 | -0.0047941 | -0.0027489 | -0.0062258 | -0.0063439 | -0.0071783 | -0.0060145 | -0.0064741 | -0.008923 | -0.010293 | -0.0084625 | -0.0085925 | -0.0071957 | -0.009118 | -0.0083598 | -0.0029358 | -0.0063117 | a15 | 0.008265 | -0.0012478 | -0.0092556 | -0.010183 | -0.010327 | -0.010902 | -0.0067978 | -0.010715 | -0.011777 | -0.0087919 | -0.0036212 | -0.0053323 | -0.0070275 | -0.013284 | -0.010438 | -0.010734 | -0.0093732 | -0.0059533 | -0.0058202 | -0.0040654 | -0.0077209
a16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
a17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | a17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Dx (mm) | 0.031633 | 0.18296 | -0.011543 | 0.19647 | 0.10606 | 0 | 0.16333 | 0.080338 | 0.047799 | -0.06525 | 0.10777 | 0.014883 | -0.065389 | -0.21363 | -0.0259 | -0.052698 | -0.21407 | -0.17069 | -0.083687 | -0.077514 |  | Dx (mm) | 0.4184 | 0.40025 | -0.041803 | 0.057807 | -0.06997 | -0.11265 | -0.044745 | -0.22815 | -0.10124 | -0.1021 | 0.23187 | 0.055576 | 0.066986 | -0.1421 | -0.026836 | 0 | -0.035507 | -0.091941 | 0.033514 | -0.10971
Dy (mm) | -0.13331 | -0.050341 | 0.049472 | 0.070725 | 0.022083 | 0.071122 | 0.046187 | -0.056226 | -0.075813 | 0 | 0 | 0.053021 | 0 | -0.064982 | -0.089872 | 0 | 0.097444 | 0 | -0.02013 | 0 |  | Dy (mm) | 0.090327 | 0.084192 | 0.036536 | -0.11143 | 0.040839 | -0.025053 | 0.032605 | 0 | -0.025013 | -0.038978 | 0.020019 | 0.031167 | -0.080082 | -0.12062 | -0.098602 | -0.10379 | 0.010786 | 0.08387 | 0.10846 | 0.064747
Mag. len. (m) | 14.425 | [20 empty] | Mag. len. (m) | 14.4284
TF (mT/KA) | 596.2222 | [20 empty] | TF (mT/KA) | 596.268
Coil pos. (mm) | 0.020794 | [20 empty] | Coil pos. (mm) | 0.025907
Current (A) | 8.5 | [20 empty] | Current (A) | 8.5
Twist (m2 rad) | 0.0039563 | [20 empty] | Twist (m2 rad) | 0.0063238

## Harmonics
Normal:
Skew:
*10

## Work sheet
| Measured harmonics- Aperture 1 | [7 empty] | Measured harmonics- Aperture 2 | [8 empty] | Zero vector
| normal multipoles |  |  |  | skew multipoles |  |  |  | normal multipoles |  |  |  | skew multipoles
| all positions (1:20) |  | central positions (2:19) |  | all positions (1:20) |  | central positions (2:19) |  | all positions (1:20) |  | central positions (2:19) |  | all positions (1:20) |  | central positions (2:19)
| average | sigma | average | sigma | average | sigma | average | sigma | average | sigma | average | sigma | average | sigma | average | sigma
1 | [17 empty] | 0
2 | -1.5619 | 0.55044 | -1.5536 | 0.54605 | -0.27742 | 0.68886 | -0.21481 | 0.54392 | 1.8428 | 0.7197 | 1.7972 | 0.59504 | -1.5036 | 2.0034 | -1.8277 | 0.90258 |  | 0
3 | 1.1044 | 8.2966 | -0.098773 | 0.42371 | 0.41627 | 0.55018 | 0.49795 | 0.3089 | 0.67376 | 8.162 | -0.52943 | 0.66977 | 0.5126 | 0.34496 | 0.50372 | 0.36173 |  | 0
4 | -0.057948 | 0.15607 | -0.041408 | 0.12504 | -0.082625 | 0.30942 | -0.099479 | 0.26489 | 0.1485 | 0.21242 | 0.16326 | 0.20768 | 0.080879 | 0.2761 | 0.058765 | 0.26573 |  | 0
5 | -0.023051 | 1.186 | 0.227 | 0.20739 | 0.12222 | 0.54535 | 0.054975 | 0.094167 | -0.33574 | 1.2359 | -0.075643 | 0.19439 | 0.008901 | 0.76163 | -0.1101 | 0.090531 |  | 0
6 | 0.025856 | 0.086374 | 0.024045 | 0.068328 | 0.071867 | 0.10324 | 0.079046 | 0.10257 | -0.0011148 | 0.14174 | -0.0075057 | 0.099228 | 0.1778 | 0.12726 | 0.17317 | 0.12388 |  | 0
7 | 1.1761 | 0.42688 | 1.1266 | 0.064178 | 0.0076647 | 0.34123 | -0.045069 | 0.036841 | 1.1212 | 0.41566 | 1.0699 | 0.067072 | -0.0037035 | 0.40638 | -0.068389 | 0.051599 |  | 0
8 | 0.0037483 | 0.030243 | 0.0048227 | 0.032906 | 0.057705 | 0.026836 | 0.060559 | 0.01708 | -0.01858 | 0.044809 | -0.020163 | 0.027661 | -0.013169 | 0.031774 | -0.01231 | 0.031173 |  | 0
9 | 0.48031 | 0.019655 | 0.48052 | 0.011069 | -0.040622 | 0.06513 | -0.029229 | 0.015752 | 0.47466 | 0.024086 | 0.47498 | 0.01374 | -0.036341 | 0.040676 | -0.030502 | 0.021612 |  | 0
10 | 0 | 0.054762 | 0.00019591 | 0.00075626 | 0 | 0.02641 | 0.00023678 | 0.0015011 | 0 | 0.071685 | -1.6246e-05 | 0.00015863 | 0 | 0.035286 | -0.00010879 | 0.00038822 |  | 0
11 | 0.76163 | 0.031678 | 0.76796 | 0.0071072 | -0.057882 | 0.048649 | -0.064938 | 0.0095942 | 0.76059 | 0.031772 | 0.76678 | 0.0072883 | -0.056942 | 0.055019 | -0.065157 | 0.0095606 |  | 0
12 | -0.001904 | 0.0053786 | -0.0017655 | 0.0041183 | -0.0041753 | 0.004675 | -0.0040257 | 0.0038385 | 0.004742 | 0.0091719 | 0.0046523 | 0.0037939 | 0.0017948 | 0.0049277 | 0.0021031 | 0.0044194 |  | 0
13 | 0.070472 | 0.0062567 | 0.070247 | 0.0024129 | -0.0050552 | 0.005682 | -0.004136 | 0.0022491 | 0.06793 | 0.0066911 | 0.067443 | 0.0034613 | -0.0068543 | 0.0030411 | -0.0066581 | 0.0020574 |  | 0
14 | -0.0057886 | 0.0030691 | -0.0063752 | 0.00092791 | -0.0074968 | 0.0035735 | -0.0082766 | 0.0015693 | -0.0058942 | 0.0037069 | -0.0060366 | 0.00099483 | -0.0050131 | 0.0031619 | -0.005643 | 0.0019895 |  | 0
15 | 0.024183 | 0.0089633 | 0.025965 | 0.0027077 | -0.0063117 | 0.0027225 | -0.0066918 | 0.0020878 | 0.023386 | 0.0094741 | 0.025325 | 0.0021789 | -0.0077209 | 0.0048174 | -0.0084211 | 0.0031219 |  | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Coil positioning estimate
1 | [12 empty] | n | n^2 | Ap. 1 | Ap. 2
2 | [12 empty] | 2 | 4 | -0.607 | -0.31081
3 | [12 empty] | 3 | 9 | -1.0167 | -0.70884
4 | [12 empty] | 4 | 16 | -1.7038 | -1.4485
5 | [12 empty] | 5 | 25 | -1.9679 | -2.02
6 | [12 empty] | 6 | 36 | -2.4803 | -2.1994
7 | [12 empty] | 7 | 49 | -3.0236 | -2.8331
8 | [12 empty] | 8 | 64 | -3.742 | -3.528
9 | [12 empty] | 9 | 81 | -4.3272 | -4.061
10 | [12 empty] | sigma (mm) |  | 0.020794 | 0.025907
11
12
13
14
15
16
17
| Random harmonics | [6 empty] | Expected harmonics (no uncertainty)
| d (mm) |  |  |  | sig(n)=d alpha beta^n |  |  | normal |  |  | skew
| 0.1 | 0.025 | 0.006 |  |  |  |  | min | ave | max | min | ave | max
1 | 4.6023 | 1.1506 | 0.27614 |  | Scaling law constants |  |  | 0 | 0 | 0 | 0 | 0 | 0
2 | 2.8314 | 0.70784 | 0.16988 |  | alpha | 73.9 |  | 0 | 0 | 0 | 0 | 0 | 0
3 | 1.7207 | 0.43017 | 0.10324 |  | beta | 0.6266 |  | 0 | 0 | 0 | 0 | 0 | 0
4 | 1.033 | 0.25824 | 0.061978 |  | gamma | 0.9939 |  | 0 | 0 | 0 | 0 | 0 | 0
5 | 0.61258 | 0.15315 | 0.036755 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
6 | 0.35886 | 0.089715 | 0.021532 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
7 | 0.20767 | 0.051917 | 0.01246 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
8 | 0.11871 | 0.029678 | 0.0071228 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
9 | 0.067037 | 0.016759 | 0.0040222 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
10 | 0.037395 | 0.0093488 | 0.0022437 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
11 | 0.020607 | 0.0051516 | 0.0012364 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
12 | 0.011217 | 0.0028042 | 0.00067302 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | ten times !
13 | 0.0060316 | 0.0015079 | 0.0003619 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | ten times !
14 | 0.0032039 | 0.00080097 | 0.00019223 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | ten times !
15 | 0.0016811 | 0.00042029 | 0.00010087 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | ten times !
16 | 0.0008714 | 0.00021785 | 5.2284e-05 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | ten times !
17 | 0.00044619 | 0.00011155 | 2.6771e-05 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | ten times !
Measured harmonics along the axis with local feed down - Aperture 1 - Normal
| position 1 | position 2 | position 3 | position 4 | position 5 | position 6 | position 7 | position 8 | position 9 | position 10 | position 11 | position 12 | position 13 | position 14 | position 15 | position 16 | position 17 | position 18 | position 19 | position 20 | integral
1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
2 | -1.2191 | -1.8588 | -1.7914 | -2.0642 | -1.652 | -1.2586 | -1.9927 | -2.0641 | -2.057 | -0.7281 | -2.1072 | -1.5933 | -1.2153 | -1.1448 | -1.4794 | -1.2708 | -0.086057 | -1.4667 | -2.1342 | -2.3059 | -1.5619
3 | 36.909 | -0.51075 | -0.16926 | 0.18138 | -0.13861 | -0.36009 | 1.0196 | 0.057138 | 0.058632 | 0.21767 | -0.0090464 | -0.51786 | -0.075721 | -0.90362 | -0.15102 | -0.020044 | 0.40888 | -0.4933 | -0.37189 | -0.72766 | 1.1044
4 | -0.11988 | 0.048926 | 0.12954 | -0.13385 | -0.11151 | -0.13804 | -0.14555 | -0.15909 | 0.0033404 | 0.094229 | -0.077973 | 0.16931 | 0.058179 | -0.15805 | -0.24125 | -0.083492 | 0.00075156 | 0.1486 | -0.14941 | -0.56342 | -0.057948
5 | -3.6823 | 0.013854 | -0.30293 | 0.14314 | 0.14025 | 0.35209 | 0.22263 | 0.34169 | 0.19882 | 0.34305 | 0.6845 | 0.23026 | 0.27401 | 0.53271 | 0.24818 | 0.23528 | 0.041509 | 0.24424 | 0.14267 | -3.457 | -0.023051
6 | 0.06333 | 0.077328 | 0.09339 | -0.002002 | -0.058286 | -0.084594 | 0.024131 | 0.087989 | 0.011057 | -0.10104 | 0.039763 | 0.12247 | 0.034432 | -0.058839 | -0.028471 | 0.019948 | 0.059622 | 0.11636 | 0.079558 | 0.00057899 | 0.025856
7 | 2.9664 | 0.94665 | 1.0901 | 1.1691 | 1.1205 | 1.1164 | 1.0684 | 1.1306 | 1.1599 | 1.0901 | 1.0694 | 1.12 | 1.1569 | 1.1029 | 1.1439 | 1.2043 | 1.1787 | 1.2382 | 1.1737 | 0.7804 | 1.1761
8 | -0.017807 | 0.041992 | 0.0060957 | -0.011311 | -0.014014 | -0.00032086 | -0.039156 | -0.056761 | -0.0050843 | 0.011079 | -0.021446 | 0.0027231 | 0.018657 | 0.097622 | 0.016061 | 0.03241 | 0.011212 | 0.0011468 | -0.0040956 | 0.036028 | 0.0037483
9 | 0.4205 | 0.47343 | 0.476 | 0.48773 | 0.48379 | 0.47269 | 0.47558 | 0.46489 | 0.46831 | 0.48108 | 0.4642 | 0.47253 | 0.48626 | 0.47181 | 0.49241 | 0.49433 | 0.4983 | 0.49899 | 0.487 | 0.45366 | 0.48031
10 | -8.4174e-06 | 3.0797e-05 | -2.2872e-06 | -5.1178e-05 | -1.0592e-05 | 0.0031921 | -2.4805e-05 | 1.6408e-05 | 8.6987e-06 | 0.00023458 | 0.00013667 | -1.8176e-06 | 0.00029773 | -2.6141e-05 | -3.4948e-07 | -0.00016849 | 5.1268e-05 | -0.00015889 | 2.6576e-06 | 0.00026888 | 0
11 | 0.65541 | 0.76236 | 0.75173 | 0.76177 | 0.76464 | 0.77708 | 0.77058 | 0.77721 | 0.76755 | 0.76565 | 0.7784 | 0.76871 | 0.77107 | 0.77919 | 0.7704 | 0.76549 | 0.76166 | 0.76794 | 0.76192 | 0.68338 | 0.76163
12 | -0.072789 | -0.057444 | -0.062374 | -0.030537 | 0.0016363 | -0.02206 | -0.049529 | -0.084826 | -0.021081 | -0.0011779 | -0.042356 | -0.04261 | 0.023259 | 0.07385 | 0.059081 | -0.005313 | -0.010088 | -0.049973 | 0.0037559 | 0.036739 | -0.01904 | ten times!
13 | 0.88312 | 0.71582 | 0.7566 | 0.70802 | 0.68345 | 0.69135 | 0.69857 | 0.70769 | 0.7104 | 0.6832 | 0.65215 | 0.71219 | 0.71639 | 0.65438 | 0.7031 | 0.71733 | 0.70979 | 0.70189 | 0.72215 | 0.52975 | 0.70472 | ten times!
14 | 0.033947 | -0.074881 | -0.068654 | -0.065844 | -0.060125 | -0.060005 | -0.077511 | -0.065943 | -0.05405 | -0.059196 | -0.072943 | -0.08595 | -0.056081 | -0.057963 | -0.051993 | -0.066486 | -0.058661 | -0.054641 | -0.056608 | -0.028523 | -0.057886 | ten times!
15 | -0.080025 | 0.31109 | 0.24468 | 0.26128 | 0.26214 | 0.2528 | 0.27842 | 0.2783 | 0.27706 | 0.24335 | 0.29308 | 0.27432 | 0.26013 | 0.25787 | 0.27475 | 0.23806 | 0.1874 | 0.22943 | 0.24944 | 0.061476 | 0.24183 | ten times!
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ten times!
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ten times!
Measured harmonics along the axis with local feed down- Aperture 1 - Skew
| position 1 | position 2 | position 3 | position 4 | position 5 | position 6 | position 7 | position 8 | position 9 | position 10 | position 11 | position 12 | position 13 | position 14 | position 15 | position 16 | position 17 | position 18 | position 19 | position 20 | integral
1
2 | -1.6694 | -0.54554 | -0.40356 | -0.2227 | 0.84097 | -0.4751 | -0.76979 | -0.79267 | 0.033847 | -0.14403 | 1.0372 | 0.44395 | -0.90379 | -0.15379 | -0.79489 | -0.23071 | -0.5734 | 0.0041298 | -0.21669 | -0.090307 | -0.27742
3 | -1.5822 | 0.93903 | 0.58148 | 0.57408 | 0.37598 | 0.0078147 | 0.27906 | 0.5059 | 0.9472 | 0.62256 | 0.25633 | 0.71887 | 0.33251 | 0.15775 | 0.2302 | 0.072724 | 0.81769 | 1.0358 | 0.50818 | 0.13165 | 0.41627
4 | 0.53484 | -0.27734 | -0.31489 | -0.14515 | -0.25281 | -0.59259 | -0.31722 | -0.081505 | -0.10312 | -0.38802 | -0.13209 | 0.01614 | -0.0030363 | -0.12196 | 0.56985 | 0.31004 | -0.1214 | 0.14767 | 0.016832 | -0.36368 | -0.082625
5 | 2.4328 | 0.18125 | 0.1064 | 0.0024966 | 0.019 | 0.0058879 | 0.13658 | 0.13096 | 0.2469 | -0.035907 | 0.0093039 | 0.14659 | 0.0090973 | 0.10581 | -0.088019 | -0.033857 | -0.0094435 | 0.12594 | -0.069437 | -0.24754 | 0.12222
6 | 0.11166 | -0.11937 | -0.010261 | 0.078443 | 0.084392 | -0.049167 | -0.10147 | 0.040881 | 0.1067 | 0.15835 | 0.29089 | 0.12302 | 0.13647 | 0.18411 | 0.16333 | 0.12959 | 0.048469 | 0.11232 | 0.046118 | -0.082272 | 0.071867
7 | 1.4728 | -0.070963 | -0.070574 | -0.082067 | -0.06021 | -0.0064976 | -0.079 | -0.062155 | -0.038467 | -0.008422 | 0.033715 | 0.022793 | -0.048478 | -0.052052 | -0.09215 | -0.05292 | -0.080537 | -0.0085297 | -0.054728 | 0.039652 | 0.0076647
8 | 0.040449 | 0.027627 | 0.069203 | 0.071283 | 0.044421 | 0.03394 | 0.057468 | 0.082245 | 0.072568 | 0.075237 | 0.077189 | 0.069029 | 0.047227 | 0.070999 | 0.047606 | 0.076669 | 0.066 | 0.067846 | 0.033507 | -0.00019979 | 0.057705
9 | -0.30597 | -0.042853 | -0.040615 | -0.038825 | -0.046385 | 0.0049467 | 0.0041308 | -0.036895 | -0.037585 | -0.017611 | -0.026579 | -0.022627 | -0.039655 | -0.030846 | -0.019421 | -0.024255 | -0.030386 | -0.025479 | -0.055187 | -0.090473 | -0.040622
10 | -4.4381e-05 | 5.5106e-05 | -2.6041e-06 | 1.3223e-05 | 4.0251e-06 | -0.00022826 | 3.5231e-05 | -5.6048e-06 | -5.1583e-06 | 0.0033088 | 0.0020579 | 1.1364e-06 | 0.0036475 | 2.7649e-05 | -1.5394e-05 | -0.001871 | -6.7574e-05 | -0.0026956 | 2.6938e-06 | 0.0029919 | 0
11 | 0.14825 | -0.077058 | -0.081758 | -0.078065 | -0.069879 | -0.053547 | -0.061257 | -0.054358 | -0.052986 | -0.053946 | -0.050547 | -0.059281 | -0.062984 | -0.067191 | -0.06934 | -0.069336 | -0.074397 | -0.062096 | -0.070862 | -0.061942 | -0.057882 | ten times!
12 | -0.040492 | -0.071729 | -0.045015 | -0.068842 | -0.039405 | -0.10904 | -0.090432 | -0.053602 | -0.040358 | -0.059876 | 0.067631 | -0.017259 | -0.021054 | -0.019106 | -0.050812 | -0.054594 | -0.03443 | -0.012414 | -0.0042894 | -0.037613 | -0.041753 | ten times!
13 | -0.27415 | -0.029585 | -0.052146 | -0.053946 | -0.054372 | -0.027092 | -0.028902 | -0.040148 | -0.019678 | -0.016092 | -0.021111 | -0.015071 | -0.033561 | -0.021372 | -0.080575 | -0.081631 | -0.064145 | -0.029532 | -0.075528 | -0.063317 | -0.050552 | ten times!
14 | 0.046101 | -0.072722 | -0.079056 | -0.09587 | -0.094657 | -0.096021 | -0.088578 | -0.065297 | -0.055953 | -0.088479 | -0.094584 | -0.10583 | -0.10395 | -0.099604 | -0.083191 | -0.068236 | -0.064285 | -0.063369 | -0.070115 | -0.037884 | -0.074968 | ten times!
15 | 0.010005 | -0.042833 | -0.073064 | -0.036715 | -0.044666 | -0.047941 | -0.027489 | -0.062258 | -0.063439 | -0.071783 | -0.060145 | -0.064741 | -0.08923 | -0.10293 | -0.084625 | -0.085925 | -0.071957 | -0.09118 | -0.083598 | -0.029358 | -0.063117 | ten times!
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ten times!
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ten times!
Measured harmonics along the axis with local feed down - Aperture 2 - Normal
| position 1 | position 2 | position 3 | position 4 | position 5 | position 6 | position 7 | position 8 | position 9 | position 10 | position 11 | position 12 | position 13 | position 14 | position 15 | position 16 | position 17 | position 18 | position 19 | position 20 | integral
1
2 | 1.9165 | 1.4129 | 1.6461 | 1.6813 | 1.9808 | 2.8926 | 2.3304 | 2.9184 | 2.5033 | 1.6351 | 1.2631 | 1.9514 | 2.0291 | 1.6136 | 0.66309 | 1.6641 | 1.11 | 1.1981 | 1.8567 | 1.2887 | 1.8428
3 | 35.8436 | -0.95213 | -0.81 | -0.47647 | -0.31557 | -1.7222 | 0.46459 | -0.40491 | -0.3503 | -0.77715 | -1.1526 | -1.3615 | -0.4618 | -1.1414 | -0.55594 | 0.58297 | 0.78605 | -0.86264 | -0.018632 | -0.76262 | 0.67376
4 | 0.61028 | -0.057913 | 0.22399 | 0.276 | 0.48657 | 0.17919 | 0.33288 | 0.097802 | 0.065703 | 0.47487 | 0.37105 | 0.20024 | 0.37302 | 0.093317 | -0.029685 | 0.08457 | -0.15756 | -0.26451 | 0.18919 | -0.23576 | 0.1485
5 | -4.4631 | -0.45628 | -0.2733 | -0.24393 | -0.28629 | 0.0267 | -0.108 | 0.21766 | 0.028876 | -0.38564 | 0.14911 | 0.014392 | -0.17681 | 0.17762 | -0.059787 | 0.088378 | -0.0020973 | 0.04283 | -0.11502 | -3.6115 | -0.33574
6 | -7.1684e-05 | -0.010722 | 0.090306 | 0.023515 | -0.02218 | -0.29008 | -0.04105 | -0.05648 | -0.086659 | 0.037587 | 0.040327 | -0.16712 | 0.043332 | 0.053978 | 0.043072 | 0.01559 | -0.019113 | 0.072458 | 0.13814 | -0.015079 | -0.0011148
7 | 2.8547 | 0.92313 | 0.98144 | 1.065 | 1.0892 | 0.96581 | 1.0367 | 1.18 | 1.1577 | 1.061 | 1.0472 | 1.0625 | 1.1025 | 1.1029 | 1.0511 | 1.1413 | 1.1249 | 1.1239 | 1.0423 | 0.76903 | 1.1212
8 | -0.018086 | -0.019792 | 0.054764 | -0.011663 | -0.059848 | -0.0082175 | -0.040429 | -0.023817 | -0.039914 | -0.044927 | -0.061621 | -0.036829 | -0.01543 | -0.016206 | -0.020354 | 0.0099214 | 0.0018976 | -0.033957 | 0.0034828 | 0.016527 | -0.01858
9 | 0.37999 | 0.46381 | 0.46581 | 0.46332 | 0.47814 | 0.48992 | 0.49777 | 0.48739 | 0.4931 | 0.47279 | 0.47057 | 0.47808 | 0.48888 | 0.46933 | 0.44448 | 0.45487 | 0.47572 | 0.48091 | 0.47472 | 0.42838 | 0.47466
10 | -0.00060139 | -0.00049781 | -9.7537e-07 | 2.2511e-05 | -4.9642e-06 | -1.3937e-05 | -1.3028e-06 | -0.00012226 | -3.3135e-06 | -7.3158e-06 | -0.00010746 | 4.4755e-07 | 2.0553e-06 | 4.657e-05 | 1.2409e-06 | 0.00039359 | -4.2039e-07 | -1.2987e-05 | 1.3885e-05 | 1.8108e-06 | 0
11 | 0.64336 | 0.76047 | 0.76285 | 0.7681 | 0.75872 | 0.77951 | 0.76664 | 0.76186 | 0.75919 | 0.76836 | 0.78353 | 0.77812 | 0.76691 | 0.76548 | 0.76776 | 0.75902 | 0.75983 | 0.76545 | 0.77032 | 0.68483 | 0.76059
12 | 0.016981 | 0.018671 | 0.027439 | -0.0099182 | 0.046089 | 0.1419 | 0.07505 | 0.077803 | 0.059728 | 0.085669 | 0.053341 | 0.072579 | 0.069005 | -0.010135 | 0.020039 | 0.015401 | 0.053018 | 0.02704 | 0.014684 | -0.036292 | 0.04742 | ten times!
13 | 0.88355 | 0.72217 | 0.71331 | 0.70458 | 0.69814 | 0.60824 | 0.64249 | 0.63746 | 0.64665 | 0.68673 | 0.61581 | 0.6491 | 0.69261 | 0.6532 | 0.67704 | 0.70635 | 0.69394 | 0.68552 | 0.70646 | 0.52397 | 0.6793 | ten times!
14 | 0.059182 | -0.054878 | -0.083799 | -0.080556 | -0.06576 | -0.055308 | -0.06514 | -0.061272 | -0.063994 | -0.044125 | -0.05868 | -0.060657 | -0.047994 | -0.050865 | -0.062089 | -0.058005 | -0.054068 | -0.054953 | -0.064446 | -0.049517 | -0.058942 | ten times!
15 | -0.10775 | 0.28991 | 0.26886 | 0.27223 | 0.22958 | 0.24678 | 0.24136 | 0.22345 | 0.24472 | 0.22749 | 0.28569 | 0.27043 | 0.27809 | 0.25083 | 0.26714 | 0.25966 | 0.23126 | 0.22071 | 0.25031 | 0.031618 | 0.23386 | ten times!
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ten times!
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ten times!
Measured harmonics along the axis with local feed down - Aperture 2 - Skew
| position 1 | position 2 | position 3 | position 4 | position 5 | position 6 | position 7 | position 8 | position 9 | position 10 | position 11 | position 12 | position 13 | position 14 | position 15 | position 16 | position 17 | position 18 | position 19 | position 20 | integral
1
2 | -0.46353 | -2.0807 | -2.3208 | -3.511 | -2.7618 | -0.78294 | -1.8189 | -2.9527 | -3.1887 | -0.94265 | -0.95465 | -1.9975 | -2.2362 | -1.6435 | -1.1051 | -1.6064 | -1.8895 | -0.43648 | -0.66979 | 6.1884 | -1.5036
3 | 0.63292 | 0.57143 | 0.48318 | 0.6178 | 0.77895 | 1.0976 | 0.91966 | 0.68106 | 0.47843 | 0.36358 | 0.32653 | 0.76065 | 0.69044 | 0.81138 | 0.054643 | -0.050266 | 0.037851 | 0.69206 | -0.24808 | 0.60104 | 0.5126
4 | -0.015376 | 0.21923 | -0.15222 | -0.071802 | 0.035186 | -0.48815 | 0.2472 | 0.12453 | 0.1047 | 0.26744 | 0.28949 | -0.14213 | 0.019378 | -0.54118 | 0.26773 | 0.3013 | 0.40575 | -0.070158 | 0.2415 | 0.61209 | 0.080879
5 | 3.2349 | 0.071583 | -0.00053049 | 0.0121 | -0.25381 | -0.026396 | -0.096168 | -0.085759 | -0.11347 | -0.20399 | -0.2018 | -0.081301 | -0.27892 | -0.086579 | -0.13886 | -0.1352 | -0.093012 | -0.11424 | -0.15542 | 0.10355 | 0.008901
6 | -0.072217 | 0.031905 | 0.095996 | 0.03273 | 0.16689 | 0.36939 | 0.23371 | 0.26332 | 0.30371 | 0.26314 | 0.39375 | 0.28594 | 0.21966 | 0.1392 | 0.092131 | 0.071884 | -0.043789 | 0.090249 | 0.10731 | 0.29618 | 0.1778
7 | 1.7412 | -0.067745 | -0.055292 | -0.084088 | -0.13977 | -0.12863 | -0.083947 | -0.047549 | -0.06535 | -0.13248 | -0.069736 | -0.090503 | -0.034617 | 0.042745 | -0.073568 | -0.099331 | -0.11307 | 0.046627 | -0.034708 | 0.044646 | -0.0037035
8 | -0.0094788 | 0.023501 | -0.0037636 | 0.015268 | -0.013641 | -0.087821 | 0.017078 | 0.019668 | 0.041046 | -0.038875 | -0.012967 | -0.021101 | -0.0073705 | -0.0014175 | -0.028441 | -0.01568 | -0.016879 | -0.027796 | -0.06239 | -0.0090019 | -0.013169
9 | -0.20325 | -0.011013 | -0.011374 | -0.037361 | -0.056119 | -0.059722 | -0.014449 | 0.0067065 | -0.01867 | -0.023598 | -0.019582 | -0.0087504 | -0.010069 | -0.057523 | -0.067779 | -0.037339 | -0.046279 | -0.049638 | -0.026471 | -0.081083 | -0.036341
10 | -0.00034827 | -0.00013744 | 7.1753e-07 | -1.4124e-05 | 7.5497e-07 | -3.5223e-05 | 3.3763e-06 | -0.0016551 | -6.2219e-06 | -9.3151e-06 | -0.00011077 | -8.4605e-06 | 1.8172e-05 | 2.9426e-05 | -1.0653e-06 | -4.0639e-05 | 1.3515e-06 | -1.0683e-06 | 7.4502e-06 | -2.0731e-05 | 0
11 | 0.17538 | -0.076724 | -0.07974 | -0.073231 | -0.072335 | -0.079626 | -0.060446 | -0.053132 | -0.050319 | -0.06027 | -0.057657 | -0.06452 | -0.058473 | -0.051039 | -0.072369 | -0.067902 | -0.072717 | -0.057901 | -0.064431 | -0.061351 | -0.056942
12 | 0.014576 | -0.039667 | 0.001248 | -0.049859 | 0.014918 | 0.10655 | -0.0071727 | 0.0034636 | 0.024752 | 0.018602 | 0.088388 | 0.053976 | 0.033795 | 0.097851 | 0.028884 | 0.0067264 | -0.039069 | 0.013143 | 0.022021 | 0.0077928 | 0.017948 | ten times!
13 | -0.18142 | -0.057774 | -0.059653 | -0.084677 | -0.096676 | -0.072527 | -0.03672 | -0.03466 | -0.049173 | -0.072455 | -0.043561 | -0.053114 | -0.068239 | -0.043509 | -0.081029 | -0.10005 | -0.092532 | -0.083956 | -0.068151 | -0.064282 | -0.068543 | ten times!
14 | 0.027218 | -0.061189 | -0.07013 | -0.041967 | -0.042538 | -0.10364 | -0.068217 | -0.071569 | -0.041614 | -0.04961 | -0.06912 | -0.062957 | -0.052541 | -0.076559 | -0.036767 | -0.033141 | -0.015527 | -0.057059 | -0.061598 | -0.014959 | -0.050131 | ten times!
15 | 0.08265 | -0.012478 | -0.092556 | -0.10183 | -0.10327 | -0.10902 | -0.067978 | -0.10715 | -0.11777 | -0.087919 | -0.036212 | -0.053323 | -0.070275 | -0.13284 | -0.10438 | -0.10734 | -0.093732 | -0.059534 | -0.058202 | -0.040654 | -0.077209 | ten times!
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ten times!
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ten times!
Relative main field module along the axis
| position 1 | position 2 | position 3 | position 4 | position 5 | position 6 | position 7 | position 8 | position 9 | position 10 | position 11 | position 12 | position 13 | position 14 | position 15 | position 16 | position 17 | position 18 | position 19 | position 20 | integral
|  | 0.00061389 | -0.0001754 | 2.1925e-05 | -0.0001754 | -0.0001754 | 2.1925e-05 | 2.1925e-05 | 2.1925e-05 | -0.0001754 | -0.0001754 | 2.1925e-05 | -0.0001754 | 2.1925e-05 | -0.0001754 | 2.1925e-05 | -0.0001754 | 2.1925e-05 | 0.00061389 |  | 596.2222
|  | 0.0003398 | -5.4807e-05 | -5.4807e-05 | -0.00025211 | -5.4807e-05 | -5.4807e-05 | -0.00025211 | -5.4807e-05 | -5.4807e-05 | 0.0001425 | -5.4807e-05 | -5.4807e-05 | -5.4807e-05 | -5.4807e-05 | -5.4807e-05 | -5.4807e-05 | -5.4807e-05 | 0.00073442 |  | 596.268
Check Computation for Aperture1
Magnetic Length
mbh dB/B | -3606.3148
| mean 3:18 | position 1 | position 2 | position 3 | position 4 | position 5 | position 6 | position 7 | position 8 | position 9 | position 10 | position 11 | position 12 | position 13 | position 14 | position 15 | position 16 | position 17 | position 18 | position 19 | position 20 | integral
dB/B | 596.1765 | -3629.9951 | 6.9068 | -0.98668 | 0.98668 | -0.98668 | -0.98668 | 0.98668 | 0.98668 | 0.98668 | -0.98668 | -0.98668 | 0.98668 | -0.98668 | 0.98668 | -0.98668 | 0.98668 | -0.98668 | 0.98668 | 6.9068 | -3582.6344
| mean 2:19 | position 1 | position 2 | position 3 | position 4 | position 5 | position 6 | position 7 | position 8 | position 9 | position 10 | position 11 | position 12 | position 13 | position 14 | position 15 | position 16 | position 17 | position 18 | position 19 | position 20 | integral
D Angle | -0.14804 | 5.1936 | -0.13561 | -0.8482 | -1.2525 | -0.98642 | -0.71558 | -0.13937 | 0.99164 | 1.1368 | 0.83651 | 0.44483 | 0.65018 | 0.54639 | 0.6056 | 0.44305 | -0.1119 | -0.45003 | -0.2826 | -0.73274 | -0.78499
db2 | -1.5517 | -1.1065 | -0.31263 | -0.24284 | -0.5131 | -0.10297 | 0.29308 | -0.42288 | -0.5085 | -0.49651 | 0.82193 | -0.55566 | -0.047014 | 0.33696 | 0.43076 | 0.075213 | 0.28099 | 1.4459 | 0.095019 | -0.57771 | -2.2993
db3 | -0.098012 | 36.9244 | -0.41347 | -0.068732 | 0.27676 | -0.041645 | -0.25471 | 1.1162 | 0.15218 | 0.15534 | 0.31466 | 0.087814 | -0.41959 | 0.021668 | -0.80023 | -0.042929 | 0.078772 | 0.50898 | -0.39947 | -0.27157 | -0.72082
db4 | -0.041707 | -0.071183 | 0.093491 | 0.17081 | -0.085573 | -0.066447 | -0.096403 | -0.096535 | -0.10916 | 0.051718 | 0.13063 | -0.018844 | 0.20995 | 0.095672 | -0.14223 | -0.20294 | -0.044703 | 0.040795 | 0.18059 | -0.11083 | -0.50037
db5 | 0.22879 | -3.6812 | -0.20962 | -0.53216 | -0.083106 | -0.089625 | 0.12375 | -0.00078665 | 0.11598 | -0.027882 | 0.11668 | 0.45826 | -0.00021255 | 0.04507 | 0.31604 | 0.023085 | 0.0065234 | -0.18837 | 0.013362 | -0.086986 | -3.4566
db6 | 0.022558 | 0.16583 | 0.11504 | 0.067635 | 0.058389 | -0.038447 | -0.10699 | 0.064292 | 0.096325 | 0.007094 | -0.14871 | 0.057883 | 0.10535 | -0.014823 | -0.16569 | -0.064436 | -0.025002 | -0.048854 | 0.019041 | 0.021906 | -0.020754
db7 | 1.1269 | 2.9665 | -0.17378 | -0.038446 | 0.042653 | -0.0063318 | -0.011893 | -0.059908 | 0.0039382 | 0.034829 | -0.036671 | -0.057389 | -0.0085768 | 0.029931 | -0.026661 | 0.017883 | 0.077024 | 0.051423 | 0.11406 | 0.047906 | 0.77977
db8 | 0.0044161 | -0.030943 | 0.077794 | 4.7438e-05 | 0.031267 | 0.0063219 | -0.0049094 | -0.0067016 | -0.044612 | -0.00038841 | -0.0081405 | -0.0021768 | 0.0021662 | -0.00075344 | 0.043942 | 0.0048961 | 0.015718 | -0.042285 | -0.043913 | -0.028272 | 0.019434
db9 | 0.48343 | 0.41748 | -0.0031048 | -0.0080022 | 0.012953 | 0.0030241 | -0.011961 | -0.0016686 | -0.017895 | -0.016074 | -0.0013445 | -0.016414 | -0.011491 | 0.0038381 | -0.00099196 | 0.007303 | 0.011559 | 0.022517 | 0.02255 | 0.0052036 | 0.45493
db10 | 0.0002557 | 0.023821 | 0.079507 | -0.0029778 | 0.091116 | 0.048375 | 0.0051806 | 0.07549 | 0.034657 | 0.018949 | -0.029414 | 0.04923 | 0.008324 | -0.029618 | -0.10076 | -0.015654 | -0.024157 | -0.091969 | -0.077673 | -0.038608 | -0.030889
db11 | 0.76822 | 0.65413 | -0.0058094 | -0.016382 | -0.0053449 | -0.0031607 | 0.0092017 | 0.0029178 | 0.0084408 | -0.0010541 | -0.0024321 | 0.010228 | 0.00042902 | 0.0028945 | 0.011129 | 0.0015667 | -0.0026243 | -0.0051167 | 0.0012171 | -0.0061006 | 0.68334
db12 | -0.0017875 | -0.0078914 | 0.0050413 | -0.00488 | 0.0089135 | 0.0071552 | -0.00026679 | 0.0049976 | -0.0028902 | 0.0019503 | -0.0014936 | 0.0024835 | -0.0016496 | 0.00079068 | -0.00089409 | 0.0059502 | -0.0014236 | -0.0097562 | -0.011804 | -0.0022245 | 0.00076481
db13 | 0.070435 | 0.088954 | 0.00037666 | 0.0055446 | 0.00051423 | -0.0022269 | -0.000858 | -0.00077619 | -0.00032918 | -5.7456e-06 | -0.0017536 | -0.0056067 | 0.0010777 | 0.0015549 | -0.0036918 | -0.00069691 | 0.001608 | 0.0022239 | 0.00088881 | 0.0021562 | 0.053167
db14 | -0.0062011 | 0.0032961 | 0.0032227 | -0.00059922 | 0.0040581 | 0.0025595 | 0.00048137 | 0.0022995 | 0.0011597 | 0.0014906 | -0.0010262 | 0.0015078 | -0.001775 | -0.00080787 | -0.0046829 | -0.0002106 | -0.0014806 | -0.0023912 | -0.0024882 | -0.0013174 | -0.0032447
db15 | 0.025965 | -0.0080025 | 0.0051449 | -0.0014961 | 0.00016367 | 0.00024967 | -0.00068472 | 0.0018777 | 0.0018655 | 0.0017416 | -0.0016292 | 0.0033433 | 0.0014674 | 4.8542e-05 | -0.00017746 | 0.0015108 | -0.0021589 | -0.0072249 | -0.0030217 | -0.0010202 | 0.0061476
da2 | -0.21407 | -2.2543 | -0.30842 | -0.19125 | 0.0059815 | 1.0593 | -0.26397 | -0.54502 | -0.57417 | 0.25273 | 0.065228 | 1.2545 | 0.65606 | -0.69228 | 0.063002 | -0.58003 | -0.01707 | -0.37532 | 0.19749 | -0.0067488 | -0.091552
da3 | 0.49674 | -1.5768 | 0.43311 | 0.08652 | 0.070824 | -0.12589 | -0.49066 | -0.22773 | 0.0094727 | 0.44945 | 0.13028 | -0.24292 | 0.22376 | -0.1642 | -0.33178 | -0.26525 | -0.4269 | 0.32545 | 0.53474 | 0.011719 | 0.13656
da4 | -0.099343 | 0.66837 | -0.17083 | -0.21937 | -0.042916 | -0.1522 | -0.48735 | -0.21027 | 0.015722 | -0.0045799 | -0.28808 | -0.032281 | 0.11886 | 0.096207 | -0.035889 | 0.6644 | 0.40983 | -0.020318 | 0.24218 | 0.11689 | -0.3592
da5 | 0.053813 | 2.4262 | 0.11781 | 0.053864 | -0.04371 | -0.032079 | -0.049691 | 0.079704 | 0.075582 | 0.19349 | -0.092763 | -0.035244 | 0.095401 | -0.047362 | 0.044471 | -0.1417 | -0.089694 | -0.070042 | 0.066445 | -0.12448 | -0.24564
da6 | 0.080358 | -0.011446 | -0.2213 | -0.071326 | 0.022135 | 0.010594 | -0.10154 | -0.16873 | -0.063589 | -0.0053707 | 0.078229 | 0.21194 | 0.063715 | 0.057256 | 0.082935 | 0.047513 | 0.050243 | 0.015455 | 0.032776 | -0.040945 | -0.083354
da7 | -0.045401 | 1.4746 | -0.026353 | -0.025465 | -0.028771 | -0.01265 | 0.038889 | -0.029036 | -0.013559 | 0.0078905 | 0.034943 | 0.082481 | 0.068832 | -0.004382 | -0.013114 | -0.047382 | -0.0091961 | -0.044884 | 0.031957 | -0.010199 | 0.039553
da8 | 0.061353 | 0.009668 | -0.049235 | 0.01914 | 0.023396 | -0.014148 | -0.011633 | 0.0071455 | 0.0070942 | -0.006342 | 0.01443 | 0.014484 | 0.019296 | -0.012899 | -0.0025967 | -0.03428 | 0.015918 | 0.031992 | 0.008565 | -0.030328 | 0.0031091
da9 | -0.02937 | -0.30846 | -0.018607 | -0.011453 | -0.0036722 | -0.016134 | 0.034522 | 0.036653 | -0.0097666 | -0.0098895 | 0.011574 | 0.0027272 | 0.0071688 | -0.010495 | 0.0044038 | 0.011225 | 0.0051076 | -0.011774 | 0.0035725 | -0.025163 | -0.090711
da10 | 0.0015132 | -0.048571 | -0.03247 | 0.02092 | 0.02119 | 0.0040595 | 0.030783 | 0.013523 | -0.029788 | -0.037228 | 0.0038565 | -0.0026307 | 0.021941 | 0.0045537 | -0.022933 | -0.041167 | -0.0012403 | 0.051664 | 0.0020154 | -0.0070521 | 0.0058084
da11 | -0.065075 | 0.14866 | -0.0133 | -0.016883 | -0.013209 | -0.0049571 | 0.011434 | 0.0031488 | 0.010451 | 0.011837 | 0.011379 | 0.014984 | 0.0056846 | 0.0021748 | -0.0013165 | -0.00435 | -0.0040854 | -0.010401 | 0.0030856 | -0.0056779 | -0.06177
da12 | -0.0038882 | -0.013036 | -0.0063347 | 0.002084 | -0.0003987 | 0.00054222 | -0.0035229 | -0.0033507 | -0.0044985 | -0.0039831 | -0.0020448 | 0.010428 | 0.0048184 | 0.0019148 | -0.001078 | -0.0054816 | -0.0012773 | 0.0064185 | 0.0029231 | 0.0028412 | -0.0034265
da13 | -0.0042214 | -0.027618 | 8.9297e-05 | -0.0011901 | -0.0025901 | -0.002038 | 0.0012011 | 0.00017316 | -8.2275e-05 | 0.0022498 | 0.0030344 | 0.0012868 | 0.0022832 | 0.001361 | 0.0041818 | -0.003194 | -0.0036818 | -0.0022349 | 0.001928 | -0.0027773 | -0.0061182
da14 | -0.0080958 | 0.0055147 | -0.0011115 | 0.0012566 | -0.00056342 | -0.0012832 | -2.559e-05 | -7.2656e-05 | -0.00013437 | 0.00052098 | -0.00036631 | -0.0018964 | -0.0013683 | -0.0018185 | -0.0014336 | -0.0020763 | 0.0016452 | 0.0044397 | 0.0030407 | 0.001247 | -0.003601
da15 | -0.0066918 | 0.0010005 | 0.0024084 | -0.00061463 | 0.0030203 | 0.0022251 | 0.0018977 | 0.0039429 | 0.00046602 | 0.00034793 | -0.00048649 | 0.00067733 | 0.00021772 | -0.0022313 | -0.0036015 | -0.0017707 | -0.0019007 | -0.00050395 | -0.0024262 | -0.001668 | -0.0029358
Check Computation for Aperture2
Magnetic Length
mbh dB/B | -3584.175
| mean 3:18 | position 1 | position 2 | position 3 | position 4 | position 5 | position 6 | position 7 | position 8 | position 9 | position 10 | position 11 | position 12 | position 13 | position 14 | position 15 | position 16 | position 17 | position 18 | position 19 | position 20 | integral
dB/B | 596.2279 | -3575.2957 | 4.0697 | 0.12332 | 0.12332 | -1.8499 | 0.12332 | 0.12332 | -1.8499 | 0.12332 | 0.12332 | 2.0965 | 0.12332 | 0.12332 | 0.12332 | 0.12332 | 0.12332 | 0.12332 | 0.12332 | 8.0161 | -3593.0544
| mean 2:19 | position 1 | position 2 | position 3 | position 4 | position 5 | position 6 | position 7 | position 8 | position 9 | position 10 | position 11 | position 12 | position 13 | position 14 | position 15 | position 16 | position 17 | position 18 | position 19 | position 20 | integral
D Angle | -0.12215 | 4.7278 | 0.0029953 | -0.90428 | -1.1277 | -0.646 | -0.54062 | -0.064323 | 0.7164 | 1.0349 | 0.55207 | 0.49818 | 0.63017 | 0.64824 | 0.72245 | 0.035475 | -0.19907 | -0.64331 | -0.34463 | -0.37097 | -0.99826
db2 | 1.797 | 3.6742 | -0.4352 | -0.14907 | -0.11091 | 0.18269 | 1.1218 | 0.52742 | 1.1323 | 0.71189 | -0.15091 | -0.56582 | 0.14268 | 0.23488 | -0.15246 | -1.1316 | -0.13358 | -0.69039 | -0.59647 | 0.062712 | 1.2941
db3 | -0.53031 | 35.848 | -0.43221 | -0.28036 | 0.055343 | 0.20838 | -1.1976 | 0.99084 | 0.12196 | 0.17934 | -0.25362 | -0.60772 | -0.82844 | 0.073086 | -0.62479 | -0.020774 | 1.1188 | 1.3166 | -0.32706 | 0.50828 | -0.76617
db4 | 0.16046 | 0.10494 | -0.2617 | 0.066247 | 0.1125 | 0.33332 | 0.017447 | 0.17435 | -0.07489 | -0.096301 | 0.32166 | 0.21989 | 0.040469 | 0.20465 | -0.075751 | -0.19303 | -0.0792 | -0.31777 | -0.4235 | 0.031607 | -0.14382
db5 | -0.073025 | -4.4252 | -0.37006 | -0.20239 | -0.17054 | -0.21453 | 0.11334 | -0.036602 | 0.30089 | 0.10791 | -0.30964 | 0.22843 | 0.08233 | -0.098014 | 0.25381 | 0.014629 | 0.16232 | 0.071391 | 0.11191 | -0.045185 | -3.6159
db6 | -0.012708 | 0.36798 | 0.13564 | 0.089252 | 0.054629 | -0.034391 | -0.31689 | -0.043744 | -0.13937 | -0.11601 | 0.010204 | 0.13917 | -0.13258 | 0.081087 | 0.013275 | 0.04334 | 0.024647 | -0.020074 | 0.047292 | 0.16452 | -0.045865
db7 | 1.0714 | 2.8678 | -0.13744 | -0.090777 | -0.0068259 | 0.019985 | -0.10486 | -0.034069 | 0.11588 | 0.089337 | -0.0082339 | -0.024948 | -0.0092259 | 0.030279 | 0.033256 | -0.021895 | 0.068349 | 0.053686 | 0.054715 | -0.02721 | 0.76894
db8 | -0.022302 | 0.070148 | 0.09698 | 0.06811 | 0.021066 | -0.052205 | -0.012742 | -0.028379 | -0.055172 | -0.041423 | -0.045852 | 0.013641 | -0.0018915 | 0.021787 | -0.02822 | -0.0067165 | 0.03041 | 0.016482 | -0.03036 | 0.034485 | -0.0030947
db9 | 0.47858 | 0.40953 | 0.023275 | -0.012746 | -0.017721 | 0.00019121 | 0.014411 | 0.019364 | 0.021182 | 0.016876 | -0.003506 | 0.0051957 | 7.9406e-05 | 0.009641 | -0.0073594 | -0.036136 | -0.026258 | -0.0026092 | 0.0023882 | -0.0062669 | 0.42978
db10 | -0.003878 | 0.15019 | 0.18761 | -0.013165 | 0.025162 | -0.025607 | -0.048944 | -0.015139 | -0.098546 | -0.042074 | -0.043648 | 0.1116 | 0.030498 | 0.031334 | -0.063756 | -0.012435 | 0.00012237 | -0.011531 | -0.034642 | 0.023153 | -0.041861
db11 | 0.76719 | 0.65105 | -0.00064479 | -0.0044122 | 0.00018191 | -0.0086335 | 0.011818 | -0.00072939 | -0.0049237 | -0.008054 | 0.00095421 | 0.018556 | 0.01115 | 0.00010481 | -0.00064719 | 0.00046601 | -0.008467 | -0.0074203 | -0.0019844 | 0.0026848 | 0.6852
db12 | 0.0043121 | 0.028899 | 0.01881 | -0.0035309 | -0.0031072 | -0.0028948 | 0.0048911 | 0.0012351 | -0.0070882 | -0.0030821 | -0.00090439 | 0.011188 | 0.0056147 | 0.0054382 | -0.012118 | -0.0041015 | -0.0034661 | -0.00068332 | -0.0055964 | -0.00060462 | -0.0074219
db13 | 0.067731 | 0.088535 | 0.0060488 | 0.0040532 | 0.0017756 | 0.0025776 | -0.006403 | -0.0030866 | -0.0021832 | -0.0024643 | 0.0013104 | -0.0061033 | -0.0028804 | 0.00088186 | -0.0021879 | -0.0002933 | 0.0024649 | 0.0018347 | 0.0015354 | 0.0031195 | 0.052866
db14 | -0.0061926 | 0.0015905 | 0.010347 | -0.0028343 | -0.0015015 | -0.001359 | -0.0018525 | -0.0010282 | -0.0041329 | -0.0024896 | -0.00041494 | 0.0058397 | 0.0015015 | 0.0024638 | -0.0031487 | -0.0014542 | -0.0005254 | 0.00019284 | -0.00056261 | 0.00095875 | -0.0050206
db15 | 0.025325 | -0.010775 | 0.0036658 | 0.001561 | 0.0018984 | -0.0023665 | -0.00064725 | -0.0011895 | -0.0029802 | -0.00085323 | -0.0025757 | 0.0032439 | 0.001718 | 0.0024836 | -0.00024163 | 0.0013892 | 0.00064138 | -0.0021986 | -0.0032541 | -0.00029448 | 0.0031618
da2 | -1.8289 | -0.050569 | -0.23382 | -0.4978 | -1.6718 | -0.94095 | 1.0363 | 0.0068947 | -1.142 | -1.3645 | 0.88553 | 0.88078 | -0.16866 | -0.39761 | 0.18797 | 0.72993 | 0.21522 | -0.059837 | 1.3765 | 1.1578 | 6.1749
da3 | 0.50501 | 0.65035 | 0.080312 | -0.019231 | 0.10675 | 0.27704 | 0.60149 | 0.41462 | 0.17081 | -0.02879 | -0.14972 | -0.16566 | 0.25534 | 0.18048 | 0.31819 | -0.45108 | -0.55677 | -0.47001 | 0.18424 | -0.74802 | 0.58866
da4 | 0.059277 | 0.21335 | 0.15877 | -0.21386 | -0.12455 | -0.022604 | -0.54671 | 0.18813 | 0.07082 | 0.048104 | 0.21675 | 0.22144 | -0.20236 | -0.04104 | -0.60256 | 0.21069 | 0.23984 | 0.34725 | -0.12614 | 0.17803 | 0.55461
da5 | -0.11078 | 3.2786 | 0.19147 | 0.10973 | 0.12132 | -0.14743 | 0.074693 | 0.010819 | 0.0070841 | -0.010547 | -0.10078 | -0.063318 | 0.032982 | -0.16605 | 0.020425 | -0.029417 | -0.024784 | 0.018061 | -0.0059085 | -0.038346 | 0.092605
da6 | 0.16951 | 0.27602 | -0.11805 | -0.060067 | -0.18037 | 0.016591 | 0.19626 | 0.077478 | 0.097777 | 0.12631 | 0.083662 | 0.22584 | 0.12632 | 0.018171 | -0.079679 | -0.11322 | -0.13938 | -0.20761 | -0.047394 | -0.022641 | 0.31205
da7 | -0.067589 | 1.7391 | 0.0096266 | 0.01291 | -0.01668 | -0.073365 | -0.056481 | -0.0175 | 0.018254 | 0.0013924 | -0.061839 | -0.0032107 | -0.023552 | 0.032268 | 0.1143 | -0.0042686 | -0.032088 | -0.045302 | 0.11264 | 0.032892 | 0.044182
da8 | -0.013436 | -0.027275 | 0.057085 | 0.017919 | 0.003442 | 0.010891 | -0.077088 | 0.038473 | 0.032455 | 0.049489 | -0.033103 | 0.0030341 | -0.00085332 | -0.012731 | -0.011423 | -0.034698 | -0.024337 | -0.00025042 | 0.0069308 | -0.025234 | 0.0084436
da9 | -0.029542 | -0.1788 | 0.030949 | 0.017432 | -0.010691 | -0.028 | -0.02911 | 0.014379 | 0.035586 | 0.011919 | 0.0076811 | 0.011285 | 0.021589 | 0.016946 | -0.019892 | -0.036769 | -0.00759 | -0.016943 | -0.023797 | 0.0050276 | -0.084264
da10 | -0.003856 | 0.077972 | 0.023821 | 0.022212 | -0.048965 | 0.025063 | -0.0023245 | 0.020148 | 0.0093467 | -0.0043156 | -0.010139 | 0.0053412 | 0.016023 | -0.034596 | -0.046252 | -0.039528 | -0.042508 | 0.010195 | 0.044761 | 0.051719 | 0.030073
da11 | -0.065118 | 0.17767 | -0.010743 | -0.014662 | -0.0086031 | -0.0073612 | -0.015391 | 0.0047627 | 0.011874 | 0.014671 | 0.0047325 | 0.0089808 | 0.0010356 | 0.0061039 | 0.014278 | -0.0072353 | -0.002841 | -0.0075013 | 0.0067918 | 0.0011082 | -0.061925
da12 | 0.0017112 | 0.0022276 | -0.0032407 | 0.00044284 | -0.012496 | 0.0022889 | 0.008356 | -0.0008254 | -0.00095116 | -6.9208e-05 | -0.0012704 | 0.0070776 | 0.0048907 | -0.0025402 | 0.0027498 | -0.0033762 | -0.0061815 | -0.004856 | 0.0042597 | 0.0057411 | 0.0037063
da13 | -0.0065169 | -0.016507 | -0.00037646 | 0.00048761 | -0.0016125 | -0.003232 | 0.00026788 | 0.0028676 | 0.0039484 | 0.0020509 | -0.00014493 | 0.00089073 | 0.00084532 | -0.00046159 | 0.0039614 | -0.00089415 | -0.0029552 | -0.0027566 | -0.0020496 | -0.00083689 | -0.0065962
da14 | -0.0055067 | 0.0047681 | 0.00098661 | -0.00037866 | -0.001673 | 0.0026201 | -0.0043552 | -0.00041648 | 0.00036308 | 0.001823 | 0.00055469 | -0.0016258 | -0.00033893 | -0.001969 | -0.0030863 | -0.00010861 | -2.6935e-05 | 0.0044336 | 0.001776 | 0.001422 | -0.00095995
da15 | -0.0084211 | 0.008265 | 0.0071733 | -0.00083449 | -0.0017623 | -0.0019055 | -0.0024806 | 0.0016234 | -0.0022939 | -0.0033556 | -0.0003708 | 0.0047999 | 0.0030888 | 0.0013936 | -0.0048626 | -0.0020167 | -0.0023132 | -0.00095206 | 0.0024678 | 0.002601 | -0.0040654
Field Colinearity | 0.012573
b1 |  | b3 |  | b5 |  | b7 |  | b9 |  | b11
inner | outer | inner | outer | inner | outer | inner | outer | inner | outer | inner | outer
59 | 40.2 | 21.8 | 16.2 | -4 | -0.77 | 1.5 | -0.22 | -0.56 | 0.031 | 0.083 | 0
Sensitivity to shims
New cross section bounds ? | yes
Twist Integral Aperture 1
Effective length (m) | 15 | 14.25 | 13.5 | 12.75 | 12 | 11.25 | 10.5 | 9.75 | 9 | 8.25 | 7.5 | 6.75 | 6 | 5.25 | 4.5 | 3.75 | 3 | 2.25 | 1.5 | 0.75
a1 angle (mrad) | 5.0455 | -0.28366 | -0.99624 | -1.4006 | -1.1345 | -0.86363 | -0.28741 | 0.8436 | 0.98871 | 0.68847 | 0.29679 | 0.50213 | 0.39834 | 0.45756 | 0.29501 | -0.25994 | -0.59808 | -0.43064 | -0.88079 | -0.93303
Twist (m2 mrad) | 37.8413 | -4.0421 | -13.4493 | -17.857 | -13.6136 | -9.7158 | -3.0178 | 8.2251 | 8.8984 | 5.6799 | 2.2259 | 3.3894 | 2.3901 | 2.4022 | 1.3275 | -0.97479 | -1.7942 | -0.96894 | -1.3212 | -0.34989
Twist Integral (I0) (m2 rad) | 0.0039563
Twist Integral Aperture 2
Effective length (m) | 15 | 14.25 | 13.5 | 12.75 | 12 | 11.25 | 10.5 | 9.75 | 9 | 8.25 | 7.5 | 6.75 | 6 | 5.25 | 4.5 | 3.75 | 3 | 2.25 | 1.5 | 0.75
a1 angle (mrad) | 4.6056 | -0.11916 | -1.0264 | -1.2498 | -0.76816 | -0.66277 | -0.18648 | 0.59425 | 0.91275 | 0.42992 | 0.37603 | 0.50802 | 0.52609 | 0.6003 | -0.086677 | -0.32122 | -0.76546 | -0.46679 | -0.49312 | -1.1204
Twist (m2 mrad) | 34.542 | -1.698 | -13.8568 | -15.9353 | -9.2179 | -7.4562 | -1.958 | 5.7939 | 8.2147 | 3.5468 | 2.8202 | 3.4291 | 3.1565 | 3.1516 | -0.39005 | -1.2046 | -2.2964 | -1.0503 | -0.73968 | -0.42015
Twist Integral (I0) (m2 rad) | 0.0063238

## Alstom Bound
Bound Parameters
| Mean | Sigma | Ybound | Rbound |  |  | Mean | Sigma | Ybound | Rbound
Magnetic Length (mm) | 14.45 | 0.01 | 3.5 | 7 | Field Colinearity |  | 0 | 0.32 | 3.5 | 7
dB/B Heads CS+NCS (units) | -3750 | 130 | 3.5 | 7
| Mean Value (3:18) (mT/kA) |  |  |  | dB/B Inner Positions 3 to 18 (units) |  |  |  | dB/B Head CS (units) |  |  |  | dB/B Head NCS (units) |  |  |  | dB/B Horn positions 2 and 19 (units)
| Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound
Main Field Component | 595.85 | 0.36 | 4 | 8 | 0 | 1.5 | 4 | 8 | -3848.5 | 151 | 3.5 | 7 | -3657.5 | 284 | 3.5 | 7 | 8.2 | 2 | 3.5 | 7
| Mean Value (2:19) |  |  |  | Inner Positions 2 to 19 minus mean value |  |  |  | Head CS |  |  |  | Head NCS
| Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound
Delta Angle (mrad) | 0 | 0 | 3.5 | 7 | 0 | 0.5 | 4 | 8 | 5 | 2 | 3.5 | 7 | -0.4 | 1 | 3.5 | 7
b2 (units) | 0 | 0.64 | 3.5 | 7 | 0 | 0.6 | 4 | 8 | 0 | 5 | 3.5 | 7 | 0 | 2 | 3.5 | 7
b3 (units) | -4 | 2 | 3.5 | 7 | 0 | 0.6 | 4 | 8 | 39 | 4.6 | 3.5 | 7 | -11.57 | 2.5 | 3.5 | 7
b4 (units) | 0 | 0.14 | 3.5 | 7 | 0 | 0.16 | 4 | 8 | 0 | 0.9 | 3.5 | 7 | 0 | 0.38 | 3.5 | 7
b5 (units) | 0.04 | 0.5 | 3.5 | 7 | 0 | 0.16 | 4 | 8 | -1.75 | 1.3 | 3.5 | 7 | -2.3 | 0.7 | 3.5 | 7
b6 (units) | 0 | 0.054 | 3.5 | 7 | 0 | 0.07 | 4 | 8 | 0 | 0.34 | 3.5 | 7 | 0 | 0.1 | 3.5 | 7
b7 (units) | 1.03 | 0.09 | 3.5 | 7 | 0 | 0.054 | 4 | 8 | 3.01 | 0.3 | 3.5 | 7 | 0.82 | 0.2 | 3.5 | 7
b8 (units) | 0 | 0.02 | 3.5 | 7 | 0 | 0.034 | 4 | 8 | 0 | 0.1 | 3.5 | 7 | 0 | 0.05 | 3.5 | 7
b9 (units) | 0.53 | 0.03 | 3.5 | 7 | 0 | 0.02 | 4 | 8 | 0.566 | 0.05 | 3.5 | 7 | 0.43 | 0.06 | 3.5 | 7
b10 (units) | 0 | 0.0045 | 3.5 | 7 | 0 | 0.04 | 4 | 8 | 0 | 0.1 | 3.5 | 7 | 0 | 0.075 | 3.5 | 7
b11 (units) | 0.74 | 0.011 | 3.5 | 7 | 0 | 0.0059 | 4 | 8 | 0.632 | 0.03 | 3.5 | 7 | 0.65 | 0.018 | 3.5 | 7
b12 (units) | 0 | 0.0018 | 3.5 | 7 | 0 | 0.0061 | 4 | 8 | 0 | 0.015 | 3.5 | 7 | 0 | 0.01 | 3.5 | 7
b13 (units) | 0.085 | 0.0083 | 3.5 | 7 | 0 | 0.0025 | 4 | 8 | 0.0924 | 0.01 | 3.5 | 7 | 0.059 | 0.009 | 3.5 | 7
b14 (units) | 0 | 0.006 | 3.5 | 7 | 0 | 0.0034 | 4 | 8 | 0 | 0.006 | 3.5 | 7 | 0 | 0.0035 | 3.5 | 7
b15 (units) | 0.034 | 0.007 | 3.5 | 7 | 0 | 0.0027 | 4 | 8 | -0.0018 | 0.006 | 3.5 | 7 | 0.0129 | 0.0068 | 3.5 | 7
a2 (units) | 0 | 1 | 3.5 | 7 | 0 | 1.1 | 4 | 8 | 0 | 6 | 3.5 | 7 | 0 | 3 | 3.5 | 7
a3 (units) | -0.13 | 0.35 | 3.5 | 7 | 0 | 0.35 | 4 | 8 | -1.7 | 2.1 | 3.5 | 7 | 1.35 | 0.7 | 3.5 | 7
a4 (units) | 0 | 0.27 | 3.5 | 7 | 0 | 0.27 | 4 | 8 | -0.853 | 1.6 | 3.5 | 7 | 0 | 0.7 | 3.5 | 7
a5 (units) | 0 | 0.14 | 3.5 | 7 | 0 | 0.12 | 4 | 8 | 2.4 | 0.83 | 3.5 | 7 | -0.18 | 0.25 | 3.5 | 7
a6 (units) | 0 | 0.12 | 3.5 | 7 | 0 | 0.068 | 4 | 8 | 0 | 0.4 | 3.5 | 7 | 0 | 0.17 | 3.5 | 7
a7 (units) | 0.005 | 0.03 | 3.5 | 7 | 0 | 0.056 | 4 | 8 | 1.9 | 0.25 | 3.5 | 7 | -0.0102 | 0.077 | 3.5 | 7
a8 (units) | -0.02 | 0.035 | 3.5 | 7 | 0 | 0.025 | 4 | 8 | 0 | 0.12 | 3.5 | 7 | 0 | 0.06 | 3.5 | 7
a9 (units) | 0.015 | 0.03 | 3.5 | 7 | 0 | 0.021 | 4 | 8 | -0.114 | 0.05 | 3.5 | 7 | 0 | 0.024 | 3.5 | 7
a10 (units) | 0.002 | 0.003 | 3.5 | 7 | 0 | 0.034 | 4 | 8 | 0 | 0.085 | 3.5 | 7 | 0 | 0.045 | 3.5 | 7
a11 (units) | 0.0127 | 0.03 | 3.5 | 7 | 0 | 0.009 | 4 | 8 | 0.2 | 0.025 | 3.5 | 7 | 0 | 0.026 | 3.5 | 7
a12 (units) | 0 | 0.005 | 3.5 | 7 | 0 | 0.0056 | 4 | 8 | 0 | 0.015 | 3.5 | 7 | 0 | 0.006 | 3.5 | 7
a13 (units) | 0 | 0.004 | 3.5 | 7 | 0 | 0.0022 | 4 | 8 | 0 | 0.01 | 3.5 | 7 | 0 | 0.0037 | 3.5 | 7
a14 (units) | -0.012 | 0.006 | 3.5 | 7 | 0 | 0.003 | 4 | 8 | 0 | 0.006 | 3.5 | 7 | -0.003 | 0.004 | 3.5 | 7
a15 (units) | 0 | 0.005 | 3.5 | 7 | 0 | 0.003 | 4 | 8 | 0 | 0.01 | 3.5 | 7 | 0 | 0.006 | 3.5 | 7
Bound Limits
| Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit |  |  | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit
Magnetic Length (mm) | 14.415 | 14.485 | 14.38 | 14.52 | Field Colinearity |  | -1.12 | 1.12 | -2.24 | 2.24
dB/B Heads CS+NCS (units) | -4205 | -3295 | -4660 | -2840
| Mean Value (3:18) (mT/kA) |  |  |  | dB/B Inner Positions 3 to 18 (units) |  |  |  | dB/B Head CS (units) |  |  |  | dB/B Head NCS (units) |  |  |  | dB/B Horn positions 2 and 19 (units)
| Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit
Main Field Component | 594.41 | 597.29 | 592.97 | 598.73 | -6 | 6 | -12 | 12 | -4377 | -3320 | -4905.5 | -2791.5 | -4651.5 | -2663.5 | -5645.5 | -1669.5 | 1.2 | 15.2 | -5.8 | 22.2
| Mean Value (2:19) |  |  |  | Inner Positions 2 to 19 minus mean value |  |  |  | Head CS |  |  |  | Head NCS
| Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit
Delta Angle (mrad) | 0 | 0 | 0 | 0 | -2 | 2 | -4 | 4 | -2 | 12 | -9 | 19 | -3.9 | 3.1 | -7.4 | 6.6
b2 (units) | -2.24 | 2.24 | -4.48 | 4.48 | -2.4 | 2.4 | -4.8 | 4.8 | -17.5 | 17.5 | -35 | 35 | -7 | 7 | -14 | 14
b3 (units) | -11 | 3 | -18 | 10 | -2.4 | 2.4 | -4.8 | 4.8 | 22.9 | 55.1 | 6.8 | 71.2 | -20.32 | -2.82 | -29.07 | 5.93
b4 (units) | -0.49 | 0.49 | -0.98 | 0.98 | -0.64 | 0.64 | -1.28 | 1.28 | -3.15 | 3.15 | -6.3 | 6.3 | -1.33 | 1.33 | -2.66 | 2.66
b5 (units) | -1.71 | 1.79 | -3.46 | 3.54 | -0.64 | 0.64 | -1.28 | 1.28 | -6.3 | 2.8 | -10.85 | 7.35 | -4.75 | 0.15 | -7.2 | 2.6
b6 (units) | -0.189 | 0.189 | -0.378 | 0.378 | -0.28 | 0.28 | -0.56 | 0.56 | -1.19 | 1.19 | -2.38 | 2.38 | -0.35 | 0.35 | -0.7 | 0.7
b7 (units) | 0.715 | 1.345 | 0.4 | 1.66 | -0.216 | 0.216 | -0.432 | 0.432 | 1.96 | 4.06 | 0.91 | 5.11 | 0.12 | 1.52 | -0.58 | 2.22
b8 (units) | -0.07 | 0.07 | -0.14 | 0.14 | -0.136 | 0.136 | -0.272 | 0.272 | -0.35 | 0.35 | -0.7 | 0.7 | -0.175 | 0.175 | -0.35 | 0.35
b9 (units) | 0.425 | 0.635 | 0.32 | 0.74 | -0.08 | 0.08 | -0.16 | 0.16 | 0.391 | 0.741 | 0.216 | 0.916 | 0.22 | 0.64 | 0.01 | 0.85
b10 (units) | -0.01575 | 0.01575 | -0.0315 | 0.0315 | -0.16 | 0.16 | -0.32 | 0.32 | -0.35 | 0.35 | -0.7 | 0.7 | -0.2625 | 0.2625 | -0.525 | 0.525
b11 (units) | 0.7015 | 0.7785 | 0.663 | 0.817 | -0.0236 | 0.0236 | -0.0472 | 0.0472 | 0.527 | 0.737 | 0.422 | 0.842 | 0.587 | 0.713 | 0.524 | 0.776
b12 (units) | -0.0063 | 0.0063 | -0.0126 | 0.0126 | -0.0244 | 0.0244 | -0.0488 | 0.0488 | -0.0525 | 0.0525 | -0.105 | 0.105 | -0.035 | 0.035 | -0.07 | 0.07
b13 (units) | 0.05595 | 0.11405 | 0.0269 | 0.1431 | -0.01 | 0.01 | -0.02 | 0.02 | 0.0574 | 0.1274 | 0.0224 | 0.1624 | 0.0275 | 0.0905 | -0.004 | 0.122
b14 (units) | -0.021 | 0.021 | -0.042 | 0.042 | -0.0136 | 0.0136 | -0.0272 | 0.0272 | -0.021 | 0.021 | -0.042 | 0.042 | -0.01225 | 0.01225 | -0.0245 | 0.0245
b15 (units) | 0.0095 | 0.0585 | -0.015 | 0.083 | -0.0108 | 0.0108 | -0.0216 | 0.0216 | -0.0228 | 0.0192 | -0.0438 | 0.0402 | -0.0109 | 0.0367 | -0.0347 | 0.0605
a2 (units) | -3.5 | 3.5 | -7 | 7 | -4.4 | 4.4 | -8.8 | 8.8 | -21 | 21 | -42 | 42 | -10.5 | 10.5 | -21 | 21
a3 (units) | -1.355 | 1.095 | -2.58 | 2.32 | -1.4 | 1.4 | -2.8 | 2.8 | -9.05 | 5.65 | -16.4 | 13 | -1.1 | 3.8 | -3.55 | 6.25
a4 (units) | -0.945 | 0.945 | -1.89 | 1.89 | -1.08 | 1.08 | -2.16 | 2.16 | -6.453 | 4.747 | -12.053 | 10.347 | -2.45 | 2.45 | -4.9 | 4.9
a5 (units) | -0.49 | 0.49 | -0.98 | 0.98 | -0.48 | 0.48 | -0.96 | 0.96 | -0.505 | 5.305 | -3.41 | 8.21 | -1.055 | 0.695 | -1.93 | 1.57
a6 (units) | -0.42 | 0.42 | -0.84 | 0.84 | -0.272 | 0.272 | -0.544 | 0.544 | -1.4 | 1.4 | -2.8 | 2.8 | -0.595 | 0.595 | -1.19 | 1.19
a7 (units) | -0.1 | 0.11 | -0.205 | 0.215 | -0.224 | 0.224 | -0.448 | 0.448 | 1.025 | 2.775 | 0.15 | 3.65 | -0.2797 | 0.2593 | -0.5492 | 0.5288
a8 (units) | -0.1425 | 0.1025 | -0.265 | 0.225 | -0.1 | 0.1 | -0.2 | 0.2 | -0.42 | 0.42 | -0.84 | 0.84 | -0.21 | 0.21 | -0.42 | 0.42
a9 (units) | -0.09 | 0.12 | -0.195 | 0.225 | -0.084 | 0.084 | -0.168 | 0.168 | -0.289 | 0.061 | -0.464 | 0.236 | -0.084 | 0.084 | -0.168 | 0.168
a10 (units) | -0.0085 | 0.0125 | -0.019 | 0.023 | -0.136 | 0.136 | -0.272 | 0.272 | -0.2975 | 0.2975 | -0.595 | 0.595 | -0.1575 | 0.1575 | -0.315 | 0.315
a11 (units) | -0.0923 | 0.1177 | -0.1973 | 0.2227 | -0.036 | 0.036 | -0.072 | 0.072 | 0.1125 | 0.2875 | 0.025 | 0.375 | -0.091 | 0.091 | -0.182 | 0.182
a12 (units) | -0.0175 | 0.0175 | -0.035 | 0.035 | -0.0224 | 0.0224 | -0.0448 | 0.0448 | -0.0525 | 0.0525 | -0.105 | 0.105 | -0.021 | 0.021 | -0.042 | 0.042
a13 (units) | -0.014 | 0.014 | -0.028 | 0.028 | -0.0088 | 0.0088 | -0.0176 | 0.0176 | -0.035 | 0.035 | -0.07 | 0.07 | -0.01295 | 0.01295 | -0.0259 | 0.0259
a14 (units) | -0.033 | 0.009 | -0.054 | 0.03 | -0.012 | 0.012 | -0.024 | 0.024 | -0.021 | 0.021 | -0.042 | 0.042 | -0.017 | 0.011 | -0.031 | 0.025
a15 (units) | -0.0175 | 0.0175 | -0.035 | 0.035 | -0.012 | 0.012 | -0.024 | 0.024 | -0.035 | 0.035 | -0.07 | 0.07 | -0.021 | 0.021 | -0.042 | 0.042

## Ansaldo Bound
Bound Parameters
| Mean | Sigma | Ybound | Rbound |  |  | Mean | Sigma | Ybound | Rbound
Magnetic Length (mm) | 14.45 | 0.01 | 3.5 | 7 | Field Colinearity |  | 0 | 0.32 | 3.5 | 7
dB/B Heads CS+NCS (units) | -3750 | 130 | 3.5 | 7
| Mean Value (3:18) (mT/kA) |  |  |  | dB/B Inner Positions 3 to 18 (units) |  |  |  | dB/B Head CS (units) |  |  |  | dB/B Head NCS (units) |  |  |  | dB/B Horn positions 2 and 19 (units)
| Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound
Main Field Component | 595.85 | 0.36 | 4 | 8 | 0 | 1.5 | 4 | 8 | -3848.5 | 151 | 3.5 | 7 | -3657.5 | 284 | 3.5 | 7 | 8.2 | 2 | 3.5 | 7
| Mean Value (2:19) |  |  |  | Inner Positions 2 to 19 minus mean value |  |  |  | Head CS |  |  |  | Head NCS
| Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound
Delta Angle (mrad) | 0 | 0 | 3.5 | 7 | 0 | 0.5 | 4 | 8 | 5 | 2 | 3.5 | 7 | -0.4 | 1 | 3.5 | 7
b2 (units) | 0 | 0.64 | 3.5 | 7 | 0 | 0.6 | 4 | 8 | 0 | 5 | 3.5 | 7 | 0 | 2 | 3.5 | 7
b3 (units) | -4 | 2 | 3.5 | 7 | 0 | 0.6 | 4 | 8 | 22.4 | 4.6 | 3.5 | 7 | -14.752 | 2.5 | 3.5 | 7
b4 (units) | 0 | 0.14 | 3.5 | 7 | 0 | 0.16 | 4 | 8 | 0 | 0.9 | 3.5 | 7 | 0 | 0.38 | 3.5 | 7
b5 (units) | 0.13 | 0.5 | 3.5 | 7 | 0 | 0.16 | 4 | 8 | -4.87 | 1.3 | 3.5 | 7 | -2.3 | 0.7 | 3.5 | 7
b6 (units) | 0 | 0.054 | 3.5 | 7 | 0 | 0.07 | 4 | 8 | 0 | 0.34 | 3.5 | 7 | 0 | 0.1 | 3.5 | 7
b7 (units) | 0.84 | 0.09 | 3.5 | 7 | 0 | 0.054 | 4 | 8 | 2.02 | 0.3 | 3.5 | 7 | 0.1505 | 0.2 | 3.5 | 7
b8 (units) | 0 | 0.02 | 3.5 | 7 | 0 | 0.034 | 4 | 8 | 0 | 0.1 | 3.5 | 7 | 0 | 0.05 | 3.5 | 7
b9 (units) | 0.48 | 0.03 | 3.5 | 7 | 0 | 0.02 | 4 | 8 | 0.447 | 0.05 | 3.5 | 7 | 0.43 | 0.06 | 3.5 | 7
b10 (units) | 0 | 0.0045 | 3.5 | 7 | 0 | 0.04 | 4 | 8 | 0 | 0.1 | 3.5 | 7 | 0 | 0.075 | 3.5 | 7
b11 (units) | 0.74 | 0.011 | 3.5 | 7 | 0 | 0.0059 | 4 | 8 | 0.55 | 0.03 | 3.5 | 7 | 0.65 | 0.018 | 3.5 | 7
b12 (units) | 0 | 0.0018 | 3.5 | 7 | 0 | 0.0061 | 4 | 8 | 0 | 0.015 | 3.5 | 7 | 0 | 0.01 | 3.5 | 7
b13 (units) | 0.085 | 0.0083 | 3.5 | 7 | 0 | 0.0025 | 4 | 8 | 0.0807 | 0.01 | 3.5 | 7 | 0.059 | 0.009 | 3.5 | 7
b14 (units) | 0 | 0.006 | 3.5 | 7 | 0 | 0.0034 | 4 | 8 | 0 | 0.006 | 3.5 | 7 | 0 | 0.0035 | 3.5 | 7
b15 (units) | 0.043 | 0.007 | 3.5 | 7 | 0 | 0.0027 | 4 | 8 | -0.00515 | 0.006 | 3.5 | 7 | 0.0244 | 0.0068 | 3.5 | 7
a2 (units) | 0 | 1 | 3.5 | 7 | 0 | 1.1 | 4 | 8 | 0 | 6 | 3.5 | 7 | 0 | 3 | 3.5 | 7
a3 (units) | -0.46 | 0.35 | 3.5 | 7 | 0 | 0.35 | 4 | 8 | -1.7 | 2.1 | 3.5 | 7 | -0.113 | 0.7 | 3.5 | 7
a4 (units) | 0 | 0.27 | 3.5 | 7 | 0 | 0.27 | 4 | 8 | 2.02 | 1.6 | 3.5 | 7 | 0 | 0.7 | 3.5 | 7
a5 (units) | 0 | 0.14 | 3.5 | 7 | 0 | 0.12 | 4 | 8 | 2.4 | 0.83 | 3.5 | 7 | -0.18 | 0.25 | 3.5 | 7
a6 (units) | 0 | 0.12 | 3.5 | 7 | 0 | 0.068 | 4 | 8 | 0 | 0.4 | 3.5 | 7 | 0 | 0.17 | 3.5 | 7
a7 (units) | 0.044 | 0.03 | 3.5 | 7 | 0 | 0.056 | 4 | 8 | 1.9 | 0.25 | 3.5 | 7 | 0.108 | 0.077 | 3.5 | 7
a8 (units) | -0.02 | 0.035 | 3.5 | 7 | 0 | 0.025 | 4 | 8 | 0 | 0.12 | 3.5 | 7 | 0 | 0.06 | 3.5 | 7
a9 (units) | 0.035 | 0.03 | 3.5 | 7 | 0 | 0.021 | 4 | 8 | -0.243 | 0.05 | 3.5 | 7 | 0 | 0.024 | 3.5 | 7
a10 (units) | 0.002 | 0.003 | 3.5 | 7 | 0 | 0.034 | 4 | 8 | 0 | 0.085 | 3.5 | 7 | 0 | 0.045 | 3.5 | 7
a11 (units) | 0.037 | 0.03 | 3.5 | 7 | 0 | 0.009 | 4 | 8 | 0.2 | 0.025 | 3.5 | 7 | 0 | 0.026 | 3.5 | 7
a12 (units) | 0 | 0.005 | 3.5 | 7 | 0 | 0.0056 | 4 | 8 | 0 | 0.015 | 3.5 | 7 | 0 | 0.006 | 3.5 | 7
a13 (units) | 0 | 0.004 | 3.5 | 7 | 0 | 0.0022 | 4 | 8 | 0 | 0.01 | 3.5 | 7 | 0 | 0.0037 | 3.5 | 7
a14 (units) | -0.012 | 0.006 | 3.5 | 7 | 0 | 0.003 | 4 | 8 | 0 | 0.006 | 3.5 | 7 | -0.003 | 0.004 | 3.5 | 7
a15 (units) | 0.0058 | 0.005 | 3.5 | 7 | 0 | 0.003 | 4 | 8 | 0 | 0.01 | 3.5 | 7 | 0 | 0.006 | 3.5 | 7
Bound Limits
| Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit |  |  | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit
Magnetic Length (mm) | 14.415 | 14.485 | 14.38 | 14.52 | Field Colinearity |  | -1.12 | 1.12 | -2.24 | 2.24
dB/B Heads CS+NCS (units) | -4205 | -3295 | -4660 | -2840
| Mean Value (3:18) (mT/kA) |  |  |  | dB/B Inner Positions 3 to 18 (units) |  |  |  | dB/B Head CS (units) |  |  |  | dB/B Head NCS (units) |  |  |  | dB/B Horn positions 2 and 19 (units)
| Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit
Main Field Component | 594.41 | 597.29 | 592.97 | 598.73 | -6 | 6 | -12 | 12 | -4377 | -3320 | -4905.5 | -2791.5 | -4651.5 | -2663.5 | -5645.5 | -1669.5 | 1.2 | 15.2 | -5.8 | 22.2
| Mean Value (2:19) |  |  |  | Inner Positions 2 to 19 minus mean value |  |  |  | Head CS |  |  |  | Head NCS
| Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit
Delta Angle (mrad) | 0 | 0 | 0 | 0 | -2 | 2 | -4 | 4 | -2 | 12 | -9 | 19 | -3.9 | 3.1 | -7.4 | 6.6
b2 (units) | -2.24 | 2.24 | -4.48 | 4.48 | -2.4 | 2.4 | -4.8 | 4.8 | -17.5 | 17.5 | -35 | 35 | -7 | 7 | -14 | 14
b3 (units) | -11 | 3 | -18 | 10 | -2.4 | 2.4 | -4.8 | 4.8 | 6.3 | 38.5 | -9.8 | 54.6 | -23.502 | -6.002 | -32.252 | 2.748
b4 (units) | -0.49 | 0.49 | -0.98 | 0.98 | -0.64 | 0.64 | -1.28 | 1.28 | -3.15 | 3.15 | -6.3 | 6.3 | -1.33 | 1.33 | -2.66 | 2.66
b5 (units) | -1.62 | 1.88 | -3.37 | 3.63 | -0.64 | 0.64 | -1.28 | 1.28 | -9.42 | -0.32 | -13.97 | 4.23 | -4.75 | 0.15 | -7.2 | 2.6
b6 (units) | -0.189 | 0.189 | -0.378 | 0.378 | -0.28 | 0.28 | -0.56 | 0.56 | -1.19 | 1.19 | -2.38 | 2.38 | -0.35 | 0.35 | -0.7 | 0.7
b7 (units) | 0.525 | 1.155 | 0.21 | 1.47 | -0.216 | 0.216 | -0.432 | 0.432 | 0.97 | 3.07 | -0.08 | 4.12 | -0.5495 | 0.8505 | -1.2495 | 1.5505
b8 (units) | -0.07 | 0.07 | -0.14 | 0.14 | -0.136 | 0.136 | -0.272 | 0.272 | -0.35 | 0.35 | -0.7 | 0.7 | -0.175 | 0.175 | -0.35 | 0.35
b9 (units) | 0.375 | 0.585 | 0.27 | 0.69 | -0.08 | 0.08 | -0.16 | 0.16 | 0.272 | 0.622 | 0.097 | 0.797 | 0.22 | 0.64 | 0.01 | 0.85
b10 (units) | -0.01575 | 0.01575 | -0.0315 | 0.0315 | -0.16 | 0.16 | -0.32 | 0.32 | -0.35 | 0.35 | -0.7 | 0.7 | -0.2625 | 0.2625 | -0.525 | 0.525
b11 (units) | 0.7015 | 0.7785 | 0.663 | 0.817 | -0.0236 | 0.0236 | -0.0472 | 0.0472 | 0.445 | 0.655 | 0.34 | 0.76 | 0.587 | 0.713 | 0.524 | 0.776
b12 (units) | -0.0063 | 0.0063 | -0.0126 | 0.0126 | -0.0244 | 0.0244 | -0.0488 | 0.0488 | -0.0525 | 0.0525 | -0.105 | 0.105 | -0.035 | 0.035 | -0.07 | 0.07
b13 (units) | 0.05595 | 0.11405 | 0.0269 | 0.1431 | -0.01 | 0.01 | -0.02 | 0.02 | 0.0457 | 0.1157 | 0.0107 | 0.1507 | 0.0275 | 0.0905 | -0.004 | 0.122
b14 (units) | -0.021 | 0.021 | -0.042 | 0.042 | -0.0136 | 0.0136 | -0.0272 | 0.0272 | -0.021 | 0.021 | -0.042 | 0.042 | -0.01225 | 0.01225 | -0.0245 | 0.0245
b15 (units) | 0.0185 | 0.0675 | -0.006 | 0.092 | -0.0108 | 0.0108 | -0.0216 | 0.0216 | -0.02615 | 0.01585 | -0.04715 | 0.03685 | 0.0006 | 0.0482 | -0.0232 | 0.072
a2 (units) | -3.5 | 3.5 | -7 | 7 | -4.4 | 4.4 | -8.8 | 8.8 | -21 | 21 | -42 | 42 | -10.5 | 10.5 | -21 | 21
a3 (units) | -1.685 | 0.765 | -2.91 | 1.99 | -1.4 | 1.4 | -2.8 | 2.8 | -9.05 | 5.65 | -16.4 | 13 | -2.563 | 2.337 | -5.013 | 4.787
a4 (units) | -0.945 | 0.945 | -1.89 | 1.89 | -1.08 | 1.08 | -2.16 | 2.16 | -3.58 | 7.62 | -9.18 | 13.22 | -2.45 | 2.45 | -4.9 | 4.9
a5 (units) | -0.49 | 0.49 | -0.98 | 0.98 | -0.48 | 0.48 | -0.96 | 0.96 | -0.505 | 5.305 | -3.41 | 8.21 | -1.055 | 0.695 | -1.93 | 1.57
a6 (units) | -0.42 | 0.42 | -0.84 | 0.84 | -0.272 | 0.272 | -0.544 | 0.544 | -1.4 | 1.4 | -2.8 | 2.8 | -0.595 | 0.595 | -1.19 | 1.19
a7 (units) | -0.061 | 0.149 | -0.166 | 0.254 | -0.224 | 0.224 | -0.448 | 0.448 | 1.025 | 2.775 | 0.15 | 3.65 | -0.1615 | 0.3775 | -0.431 | 0.647
a8 (units) | -0.1425 | 0.1025 | -0.265 | 0.225 | -0.1 | 0.1 | -0.2 | 0.2 | -0.42 | 0.42 | -0.84 | 0.84 | -0.21 | 0.21 | -0.42 | 0.42
a9 (units) | -0.07 | 0.14 | -0.175 | 0.245 | -0.084 | 0.084 | -0.168 | 0.168 | -0.418 | -0.068 | -0.593 | 0.107 | -0.084 | 0.084 | -0.168 | 0.168
a10 (units) | -0.0085 | 0.0125 | -0.019 | 0.023 | -0.136 | 0.136 | -0.272 | 0.272 | -0.2975 | 0.2975 | -0.595 | 0.595 | -0.1575 | 0.1575 | -0.315 | 0.315
a11 (units) | -0.068 | 0.142 | -0.173 | 0.247 | -0.036 | 0.036 | -0.072 | 0.072 | 0.1125 | 0.2875 | 0.025 | 0.375 | -0.091 | 0.091 | -0.182 | 0.182
a12 (units) | -0.0175 | 0.0175 | -0.035 | 0.035 | -0.0224 | 0.0224 | -0.0448 | 0.0448 | -0.0525 | 0.0525 | -0.105 | 0.105 | -0.021 | 0.021 | -0.042 | 0.042
a13 (units) | -0.014 | 0.014 | -0.028 | 0.028 | -0.0088 | 0.0088 | -0.0176 | 0.0176 | -0.035 | 0.035 | -0.07 | 0.07 | -0.01295 | 0.01295 | -0.0259 | 0.0259
a14 (units) | -0.033 | 0.009 | -0.054 | 0.03 | -0.012 | 0.012 | -0.024 | 0.024 | -0.021 | 0.021 | -0.042 | 0.042 | -0.017 | 0.011 | -0.031 | 0.025
a15 (units) | -0.0117 | 0.0233 | -0.0292 | 0.0408 | -0.012 | 0.012 | -0.024 | 0.024 | -0.035 | 0.035 | -0.07 | 0.07 | -0.021 | 0.021 | -0.042 | 0.042

## Noell Bound
Bound Parameters
| Mean | Sigma | Ybound | Rbound |  |  | Mean | Sigma | Ybound | Rbound
Magnetic Length (mm) | 14.45 | 0.01 | 3.5 | 7 | Field Colinearity |  | 0 | 0.32 | 3.5 | 7
dB/B Heads CS+NCS (units) | -3750 | 130 | 3.5 | 7
| Mean Value (3:18) (mT/kA) |  |  |  | dB/B Inner Positions 3 to 18 (units) |  |  |  | dB/B Head CS (units) |  |  |  | dB/B Head NCS (units) |  |  |  | dB/B Horn positions 2 and 19 (units)
| Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound
Main Field Component | 595.85 | 0.36 | 4 | 8 | 0 | 1.5 | 4 | 8 | -3848.5 | 151 | 3.5 | 7 | -3657.5 | 284 | 3.5 | 7 | 8.2 | 2 | 3.5 | 7
| Mean Value (2:19) |  |  |  | Inner Positions 2 to 19 minus mean value |  |  |  | Head CS |  |  |  | Head NCS
| Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound | Mean | Sigma | Ybound | Rbound
Delta Angle (mrad) | 0 | 0 | 3.5 | 7 | 0 | 0.5 | 4 | 8 | 5 | 2 | 3.5 | 7 | -0.4 | 1 | 3.5 | 7
b2 (units) | 0 | 0.64 | 3.5 | 7 | 0 | 0.6 | 4 | 8 | 0 | 5 | 3.5 | 7 | 0 | 2 | 3.5 | 7
b3 (units) | -4 | 2 | 3.5 | 7 | 0 | 0.6 | 4 | 8 | 32.9 | 4.6 | 3.5 | 7 | -5.67 | 2.5 | 3.5 | 7
b4 (units) | 0 | 0.14 | 3.5 | 7 | 0 | 0.16 | 4 | 8 | 0 | 0.9 | 3.5 | 7 | 0 | 0.38 | 3.5 | 7
b5 (units) | -0.56 | 0.5 | 3.5 | 7 | 0 | 0.16 | 4 | 8 | -3.74 | 1.3 | 3.5 | 7 | -2.3 | 0.7 | 3.5 | 7
b6 (units) | 0 | 0.054 | 3.5 | 7 | 0 | 0.07 | 4 | 8 | 0 | 0.34 | 3.5 | 7 | 0 | 0.1 | 3.5 | 7
b7 (units) | 1 | 0.09 | 3.5 | 7 | 0 | 0.054 | 4 | 8 | 2.94 | 0.3 | 3.5 | 7 | 0.589 | 0.2 | 3.5 | 7
b8 (units) | 0 | 0.02 | 3.5 | 7 | 0 | 0.034 | 4 | 8 | 0 | 0.1 | 3.5 | 7 | 0 | 0.05 | 3.5 | 7
b9 (units) | 0.46 | 0.03 | 3.5 | 7 | 0 | 0.02 | 4 | 8 | 0.582 | 0.05 | 3.5 | 7 | 0.43 | 0.06 | 3.5 | 7
b10 (units) | 0 | 0.0045 | 3.5 | 7 | 0 | 0.04 | 4 | 8 | 0 | 0.1 | 3.5 | 7 | 0 | 0.075 | 3.5 | 7
b11 (units) | 0.74 | 0.011 | 3.5 | 7 | 0 | 0.0059 | 4 | 8 | 0.603 | 0.03 | 3.5 | 7 | 0.65 | 0.018 | 3.5 | 7
b12 (units) | 0 | 0.0018 | 3.5 | 7 | 0 | 0.0061 | 4 | 8 | 0 | 0.015 | 3.5 | 7 | 0 | 0.01 | 3.5 | 7
b13 (units) | 0.085 | 0.0083 | 3.5 | 7 | 0 | 0.0025 | 4 | 8 | 0.107 | 0.01 | 3.5 | 7 | 0.059 | 0.009 | 3.5 | 7
b14 (units) | 0 | 0.006 | 3.5 | 7 | 0 | 0.0034 | 4 | 8 | 0 | 0.006 | 3.5 | 7 | 0 | 0.0035 | 3.5 | 7
b15 (units) | 0.032 | 0.007 | 3.5 | 7 | 0 | 0.0027 | 4 | 8 | -0.008 | 0.006 | 3.5 | 7 | 0.0135 | 0.0068 | 3.5 | 7
a2 (units) | 0 | 1 | 3.5 | 7 | 0 | 1.1 | 4 | 8 | 0 | 6 | 3.5 | 7 | 0 | 3 | 3.5 | 7
a3 (units) | 0.12 | 0.35 | 3.5 | 7 | 0 | 0.35 | 4 | 8 | -1.7 | 2.1 | 3.5 | 7 | 0.988 | 0.7 | 3.5 | 7
a4 (units) | 0 | 0.27 | 3.5 | 7 | 0 | 0.27 | 4 | 8 | 0.76 | 1.6 | 3.5 | 7 | 0 | 0.7 | 3.5 | 7
a5 (units) | 0 | 0.14 | 3.5 | 7 | 0 | 0.12 | 4 | 8 | 2.4 | 0.83 | 3.5 | 7 | -0.18 | 0.25 | 3.5 | 7
a6 (units) | 0 | 0.12 | 3.5 | 7 | 0 | 0.068 | 4 | 8 | 0 | 0.4 | 3.5 | 7 | 0 | 0.17 | 3.5 | 7
a7 (units) | 0.002 | 0.03 | 3.5 | 7 | 0 | 0.056 | 4 | 8 | 1.9 | 0.25 | 3.5 | 7 | -0.00256 | 0.077 | 3.5 | 7
a8 (units) | -0.02 | 0.035 | 3.5 | 7 | 0 | 0.025 | 4 | 8 | 0 | 0.12 | 3.5 | 7 | 0 | 0.06 | 3.5 | 7
a9 (units) | 0.0072 | 0.03 | 3.5 | 7 | 0 | 0.021 | 4 | 8 | -0.231 | 0.05 | 3.5 | 7 | 0 | 0.024 | 3.5 | 7
a10 (units) | 0.002 | 0.003 | 3.5 | 7 | 0 | 0.034 | 4 | 8 | 0 | 0.085 | 3.5 | 7 | 0 | 0.045 | 3.5 | 7
a11 (units) | 0.002 | 0.03 | 3.5 | 7 | 0 | 0.009 | 4 | 8 | 0.2 | 0.025 | 3.5 | 7 | 0 | 0.026 | 3.5 | 7
a12 (units) | 0 | 0.005 | 3.5 | 7 | 0 | 0.0056 | 4 | 8 | 0 | 0.015 | 3.5 | 7 | 0 | 0.006 | 3.5 | 7
a13 (units) | 0 | 0.004 | 3.5 | 7 | 0 | 0.0022 | 4 | 8 | 0 | 0.01 | 3.5 | 7 | 0 | 0.0037 | 3.5 | 7
a14 (units) | -0.012 | 0.006 | 3.5 | 7 | 0 | 0.003 | 4 | 8 | 0 | 0.006 | 3.5 | 7 | -0.003 | 0.004 | 3.5 | 7
a15 (units) | 0 | 0.005 | 3.5 | 7 | 0 | 0.003 | 4 | 8 | 0 | 0.01 | 3.5 | 7 | 0 | 0.006 | 3.5 | 7
Bound Limits
| Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit |  |  | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit
Magnetic Length (mm) | 14.415 | 14.485 | 14.38 | 14.52 | Field Colinearity |  | -1.12 | 1.12 | -2.24 | 2.24
dB/B Heads CS+NCS (units) | -4205 | -3295 | -4660 | -2840
| Mean Value (3:18) (mT/kA) |  |  |  | dB/B Inner Positions 3 to 18 (units) |  |  |  | dB/B Head CS (units) |  |  |  | dB/B Head NCS (units) |  |  |  | dB/B Horn positions 2 and 19 (units)
| Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit
Main Field Component | 594.41 | 597.29 | 592.97 | 598.73 | -6 | 6 | -12 | 12 | -4377 | -3320 | -4905.5 | -2791.5 | -4651.5 | -2663.5 | -5645.5 | -1669.5 | 1.2 | 15.2 | -5.8 | 22.2
| Mean Value (2:19) |  |  |  | Inner Positions 2 to 19 minus mean value |  |  |  | Head CS |  |  |  | Head NCS
| Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit | Inf. Y limit | Sup. Y limit | Inf. R limit | Sup. R limit
Delta Angle (mrad) | 0 | 0 | 0 | 0 | -2 | 2 | -4 | 4 | -2 | 12 | -9 | 19 | -3.9 | 3.1 | -7.4 | 6.6
b2 (units) | -2.24 | 2.24 | -4.48 | 4.48 | -2.4 | 2.4 | -4.8 | 4.8 | -17.5 | 17.5 | -35 | 35 | -7 | 7 | -14 | 14
b3 (units) | -11 | 3 | -18 | 10 | -2.4 | 2.4 | -4.8 | 4.8 | 16.8 | 49 | 0.7 | 65.1 | -14.42 | 3.08 | -23.17 | 11.83
b4 (units) | -0.49 | 0.49 | -0.98 | 0.98 | -0.64 | 0.64 | -1.28 | 1.28 | -3.15 | 3.15 | -6.3 | 6.3 | -1.33 | 1.33 | -2.66 | 2.66
b5 (units) | -2.31 | 1.19 | -4.06 | 2.94 | -0.64 | 0.64 | -1.28 | 1.28 | -8.29 | 0.81 | -12.84 | 5.36 | -4.75 | 0.15 | -7.2 | 2.6
b6 (units) | -0.189 | 0.189 | -0.378 | 0.378 | -0.28 | 0.28 | -0.56 | 0.56 | -1.19 | 1.19 | -2.38 | 2.38 | -0.35 | 0.35 | -0.7 | 0.7
b7 (units) | 0.685 | 1.315 | 0.37 | 1.63 | -0.216 | 0.216 | -0.432 | 0.432 | 1.89 | 3.99 | 0.84 | 5.04 | -0.111 | 1.289 | -0.811 | 1.989
b8 (units) | -0.07 | 0.07 | -0.14 | 0.14 | -0.136 | 0.136 | -0.272 | 0.272 | -0.35 | 0.35 | -0.7 | 0.7 | -0.175 | 0.175 | -0.35 | 0.35
b9 (units) | 0.355 | 0.565 | 0.25 | 0.67 | -0.08 | 0.08 | -0.16 | 0.16 | 0.407 | 0.757 | 0.232 | 0.932 | 0.22 | 0.64 | 0.01 | 0.85
b10 (units) | -0.01575 | 0.01575 | -0.0315 | 0.0315 | -0.16 | 0.16 | -0.32 | 0.32 | -0.35 | 0.35 | -0.7 | 0.7 | -0.2625 | 0.2625 | -0.525 | 0.525
b11 (units) | 0.7015 | 0.7785 | 0.663 | 0.817 | -0.0236 | 0.0236 | -0.0472 | 0.0472 | 0.498 | 0.708 | 0.393 | 0.813 | 0.587 | 0.713 | 0.524 | 0.776
b12 (units) | -0.0063 | 0.0063 | -0.0126 | 0.0126 | -0.0244 | 0.0244 | -0.0488 | 0.0488 | -0.0525 | 0.0525 | -0.105 | 0.105 | -0.035 | 0.035 | -0.07 | 0.07
b13 (units) | 0.05595 | 0.11405 | 0.0269 | 0.1431 | -0.01 | 0.01 | -0.02 | 0.02 | 0.072 | 0.142 | 0.037 | 0.177 | 0.0275 | 0.0905 | -0.004 | 0.122
b14 (units) | -0.021 | 0.021 | -0.042 | 0.042 | -0.0136 | 0.0136 | -0.0272 | 0.0272 | -0.021 | 0.021 | -0.042 | 0.042 | -0.01225 | 0.01225 | -0.0245 | 0.0245
b15 (units) | 0.0075 | 0.0565 | -0.017 | 0.081 | -0.0108 | 0.0108 | -0.0216 | 0.0216 | -0.029 | 0.013 | -0.05 | 0.034 | -0.0103 | 0.0373 | -0.0341 | 0.0611
a2 (units) | -3.5 | 3.5 | -7 | 7 | -4.4 | 4.4 | -8.8 | 8.8 | -21 | 21 | -42 | 42 | -10.5 | 10.5 | -21 | 21
a3 (units) | -1.105 | 1.345 | -2.33 | 2.57 | -1.4 | 1.4 | -2.8 | 2.8 | -9.05 | 5.65 | -16.4 | 13 | -1.462 | 3.438 | -3.912 | 5.888
a4 (units) | -0.945 | 0.945 | -1.89 | 1.89 | -1.08 | 1.08 | -2.16 | 2.16 | -4.84 | 6.36 | -10.44 | 11.96 | -2.45 | 2.45 | -4.9 | 4.9
a5 (units) | -0.49 | 0.49 | -0.98 | 0.98 | -0.48 | 0.48 | -0.96 | 0.96 | -0.505 | 5.305 | -3.41 | 8.21 | -1.055 | 0.695 | -1.93 | 1.57
a6 (units) | -0.42 | 0.42 | -0.84 | 0.84 | -0.272 | 0.272 | -0.544 | 0.544 | -1.4 | 1.4 | -2.8 | 2.8 | -0.595 | 0.595 | -1.19 | 1.19
a7 (units) | -0.103 | 0.107 | -0.208 | 0.212 | -0.224 | 0.224 | -0.448 | 0.448 | 1.025 | 2.775 | 0.15 | 3.65 | -0.27206 | 0.26694 | -0.54156 | 0.53644
a8 (units) | -0.1425 | 0.1025 | -0.265 | 0.225 | -0.1 | 0.1 | -0.2 | 0.2 | -0.42 | 0.42 | -0.84 | 0.84 | -0.21 | 0.21 | -0.42 | 0.42
a9 (units) | -0.0978 | 0.1122 | -0.2028 | 0.2172 | -0.084 | 0.084 | -0.168 | 0.168 | -0.406 | -0.056 | -0.581 | 0.119 | -0.084 | 0.084 | -0.168 | 0.168
a10 (units) | -0.0085 | 0.0125 | -0.019 | 0.023 | -0.136 | 0.136 | -0.272 | 0.272 | -0.2975 | 0.2975 | -0.595 | 0.595 | -0.1575 | 0.1575 | -0.315 | 0.315
a11 (units) | -0.103 | 0.107 | -0.208 | 0.212 | -0.036 | 0.036 | -0.072 | 0.072 | 0.1125 | 0.2875 | 0.025 | 0.375 | -0.091 | 0.091 | -0.182 | 0.182
a12 (units) | -0.0175 | 0.0175 | -0.035 | 0.035 | -0.0224 | 0.0224 | -0.0448 | 0.0448 | -0.0525 | 0.0525 | -0.105 | 0.105 | -0.021 | 0.021 | -0.042 | 0.042
a13 (units) | -0.014 | 0.014 | -0.028 | 0.028 | -0.0088 | 0.0088 | -0.0176 | 0.0176 | -0.035 | 0.035 | -0.07 | 0.07 | -0.01295 | 0.01295 | -0.0259 | 0.0259
a14 (units) | -0.033 | 0.009 | -0.054 | 0.03 | -0.012 | 0.012 | -0.024 | 0.024 | -0.021 | 0.021 | -0.042 | 0.042 | -0.017 | 0.011 | -0.031 | 0.025
a15 (units) | -0.0175 | 0.0175 | -0.035 | 0.035 | -0.012 | 0.012 | -0.024 | 0.024 | -0.035 | 0.035 | -0.07 | 0.07 | -0.021 | 0.021 | -0.042 | 0.042

## MTF
Straight part | [21 empty] | Integral
Aperture 1 | [10 empty] | Aperture 2 | [10 empty] | Aperture 1 | [9 empty] | Aperture 2
b2 | b3 | b4 | b5 | b7 | a1 | a2 | a3 | a4 | Coil pos. | TF | b2 | b3 | b4 | b5 | b7 | a1 | a2 | a3 | a4 | Coil pos. | TF | b2 | b3 | b4 | b5 | b7 | a1 | a2 | a3 | a4 | Mag len | b2 | b3 | b4 | b5 | b7 | a1 | a2 | a3 | a4 | Mag len
-1.5517 | -0.098012 | -0.041707 | 0.22879 | 1.1269 | -1.4804 | -0.21407 | 0.49674 | -0.099343 | 20.7936 | 0.59622 | 1.797 | -0.53031 | 0.16046 | -0.073025 | 1.0714 | -1.2215 | -1.8289 | 0.50501 | 0.059277 | 25.907 | 0.59627 | -1.5619 | 1.1044 | -0.057948 | -0.023051 | 1.1761 | 0 | -0.27742 | 0.41627 | -0.082625 | 14424.973 | 1.8428 | 0.67376 | 0.1485 | -0.33574 | 1.1212 | 0 | -1.5036 | 0.5126 | 0.080879 | 14428.416
Shims
Aperture 1 | [7 empty] | Aperture 2
Aperture 1 b2: Upper; Aperture 1 b7: Lower; Aperture 1 a4: Upper |  |  |  | Lower
Aperture 1 b2: Inner layer; Aperture 1 b4: Outer layer; Aperture 1 b7: Inner layer; Aperture 1 a2: Outer layer; Aperture 1 a4: Inner layer |  | Outer layer |  | Inner layer |  | Outer layer
Side | Central | Side | Central | Side | Central | Side | Central | Side | Central | Side | Central | Side | Central | Side | Central
0.2 | 0.2 | 0.8 | 0.8 | 0.2 | 0.2 | 0.8 | 0.8 | 0.2 | 0.2 | 0.8 | 0.8 | 0.2 | 0.2 | 0.8 | 0.8